TENDER DOCUMENT

FOR

AVAILING ELECTRICAL POWER CONNECTION WITH 250KVA POWER SUPPLY FOR HINDLABS MRI SCAN UNIT AT GOVT MEDICAL COLLEGE HOSPITAL, KOZHIKODE.

PART-III

PRICE BID

TENDER NO. HLL/CHO/HCS/MRI/2015/10/ Tender-07

10 February 2015

HLL LIFECARE LIMITED.

HEALTHCARE SERVICE DIVISION

Contents    			  	                                   Page No.

- Commercial Conditions		                                   03

- Special Conditions                      	                                   06

3               Bill of Quantities                                                               08

  - COMMERCIAL CONDITIONS

  - The tendered rate shall inter alia be deemed to include for the provision of  all  materials , process, operation and special requirements detailed in the  particular specification irrespective of whether these are mentioned in the description of equipment schedule and Bill of quantities or not. It is an express condition of the contract that the tendered rates for various items in the Bill of Quantities shall be deemed to include for the full, entire and final condition of the contractor respective items of the works in accordance with the provision of the contract.

  - The tendered rate shall include for all taxes, duties, etc. as applicable and shall be quoted on the works contract basis for Availing Electrical power connection with 250KVA power supply at GMCH,Kozhikode.

1.3	The tendered rate shall remain firm and free from variation due to rise in the cost of materials/equipment labour or any other reasons whatsoever during the contract period and valid extension.

1.4	The quantum of excise duty included in the tendered price, the rate at which they were assumed etc. shall be indicated in the tender.

  - UNIT RATES

  - Only approved work will be measured on completion and priced as per rates quoted against the respective items.

3.     BRIEF DESCRIPTION OF PRICING

  - The tenderer shall furnish duly certified breakup of material and labour separately for each item of work. The same shall be attached separately along with the price bid.

  - The quoted price shall be inclusive of all taxes and duties whether payable by the contractor or to be deducted at source. This shall include those applicable among VAT, Sales Tax, Income Tax, Customs Duty, Excise Duty, Turnover Tax, Service Tax, Work Contract Tax, Octroi, Labour Welfare Cess or any other Taxes and Duties prevailing in respect of this contract. ANY BID STATING THAT TAXES ARE EXTRA WILL BE SUMMARILY REJECTED.

- PRO-RATA VALUE

The detailed break up of prices for various items of equipments and materials of the full system should be provided by successful tenderers within fifteen days from the date of letter of intent to facilitate the Employer for assessment and verification and to certify payment.

- INCOME TAX

Any payment to the contractor as per contract, will be made after deducting income tax as per the rules and regulations.

6. 	 SALES TAX AND EXCISE DUTY

The tenderer shall clearly indicate sales tax, Excise and works contract tax and other duties as applicable in his offer for carrying out this work.

7.      SUBMISSION OF BILL

  - The contractor shall from time to time prepare and submit interim bills of the work executed and on completion of the contract, he shall prepare and submit the final bill. The measurements sheets in support of the interim and final bills shall be prepared by the contractor on the basis of measurements taken by him jointly with the project engineer and the said measurement sheets shall be submitted by him with the relevant bill.

- EXTRA ITEMS

        - The contractor is bound to carry out any items of work necessary for the completion of the job even though such items may not have been included in the schedule of probable quantities or rates, such items being necessary or essential for completing the job. Variation order in respect of such additional items and their quantities will be issued in writing by the Employer.

          - All shavings, cuttings and other rubbish as it accumulates from time to    time during the progress of work and on completion including that of the sub-contractors and special tradesman and all materials condemned by the project engineer shall be cleared and removed from the site by the contractor without any extra charge.

  - All measuring steel taps, scaffolding, ladders instruments and tools that may be required for taking measurements shall be supplied by the contractor.

- OVER TIME WORK

The owners shall provide a source for power supply at one convenient point at    site. The contractor shall at his own cost install a separate meter at the said source and lay additional cables from the said source also at his own cost. For the electricity consumed by the contractor he shall pay the owner the actual cost at the rate charged by the local authority for power for constructional purposes. The contractor shall also obtain the necessary permit for utilizing power for constructional purposes.

- TERMS OF PAYMENT

  - The rate of payment for the contract value under this contract shall be regulated  and detailed below:

50% after supply of materials at site in good working condition on pro-rata basis.

40% after completion of installation in all respects.

Balance 10% will be paid after testing, commissioning & handing over to the client,                     including all required statutory approvals.

11.1	EXECUTION WORK

11.1.1 The whole of the work as described in the contract (including bills of materials, specification and all drawings pertaining thereto) and as advised by the Owners/Employers from time is to be carried out and completed in all parts to the entire satisfaction of the Owners/Employers. Any minor details of construction which are obviously and fairly intended, or which may not have been definitely referred to in this contract, but which are usual construction practice and essential to the work, shall be included in this contact.

11.2	MAINTENANCE & TRAINING FOR PERSONNEL

11.2.1	The contractor shall without any extra cost carry out for a period of 12 months after the installation is taken over by the owners, all routine and special maintenance and attend to any difficulties and defects that may arise in the operation of the system.

11.2.2	The contractor shall associate with the Employers’ staff during erection and the maintenance period, in the maintenance/operation of the system..

11.2.3	If required, by the Employers, the contractor shall also train members of the Employers’ staff at their works/service station without any extra charge.

11.3	CERTIFICATE OF COMPLETION

11.3.1	The contractor shall intimate to HLL in writing as and when the works are completed and put into beneficial use in order to enable HLL to check certify to the Employer to take over the plants.

11.3.2	The work shall not be considered as completed and put into beneficial use until HLL have certified in writing that the same has been completed and put into beneficial use.

11.3.3	The defects liability period of one year shall commence from date of such completion or any specific date mentioned therein.

11.4	OPERATIONAL AND MAINTENANCE MANUALS

11.4.1	The contractor shall also furnish the prints of all up-dated handing over along with required set of operating/maintenance manuals/instructions.

11.5   STATUTARY APPROVALS

All statuary approvals pertaining to the installations including electrical inspector   approvals shall be in the scope of the contractor.

The electrical Inspectorate approval for the HLL units (for which 250KV supply is proposed) including external and internal electrification has to be taken by the contractor.

| Sl. No | Description | Qty | Unit | Rate in words and figures | Amount in words and figures |
| --- | --- | --- | --- | --- | --- |
| 1 | TRANSFORMER |  |  |  |  |
|  | Erection, testing and commissioning of 1 No. M/s Intrans Electro Components Pvt make unitized substation with the following features: |  |  |  |  |
|  | 1 No. 250 KVA, 11 KV/433 V, 3 phase 50 Hz copper wound Indoor type Resin Cast dry type transformer having vector group of Dyn 11 with tapings +5% to – 10 % in steps of 2.5% (with link arrangement) consisting of HT panel and LT terminal cable box conforming to IS 2026 and 11171. The HT panel consists of the following items and will be as per Kerala Electrical Inspectorate standards. • 11 KV, 250MVA, 630 Amps, LBSFU • HT HRC fuses of suitable ratings. • Earth Switch on the outgoing side • Shunt Trip Coil to operate at 230V • Space Heater • Indicating Lamps • With CT/PT & Provision for TOD meter The whole assembly shall be mounted on a rigid under base steel fabricated section. |  |  |  |  |
|  | CT PT unitswith H.T TOD Meter. (Note: Transformer need to couple existing 11KV BUS Bar) | 1 | No |  |  |
| 2 | Panel Boards |  |  |  |  |
|  | Supply, installation, testing and commissioning of extensible type LT panel (welded or bolted construction )suitable for operation on 415 V, 50 Hz AC supply fabricated out of 14 gauge CRCA section for frame work and 16 guage CRCA sheet for body covers/doors i/c providing 40x10mm aluminum bus bar and comprising the following switch gears ,metering equipment ,Earthing the panel etc complete as required. |  |  |  |  |
| 2.1 | MSB |  |  |  |  |
| a | Incomer(1): |  |  |  |  |
|  | 400A 4 Pole Microprocessor based MCCB 35kA – 1 No. |  |  |  |  |
|  | (EF Relay,MF Meter, & indicators with control fuse - 3 Nos) |  |  |  |  |
| b | Busbar |  |  |  |  |
|  | 400A TPN Aluminium bus bar - 1 Set. |  |  |  |  |
| c | Outgoing: |  |  |  |  |
|  | 250A TP MCCB – 2 No. |  |  |  |  |
|  | 200A TP MCCB – 3 Nos. |  |  |  |  |
| d | 400/5A class 1 CT -4Nos | 1 | No |  |  |
| 2.2 | SSB |  |  |  |  |
| a | Incomer: |  |  |  |  |
|  | 160A TPN Isolator – 1 No . |  |  |  |  |
|  | 160A TPN Aluminium bus bar - 1 Set . |  |  |  |  |
|  | MF meter with CT & Indicators with control fuse-3Nos |  |  |  |  |
| b | Outgoing: |  |  |  |  |
|  | 63A TP MCCB – 4Nos |  |  |  |  |
|  | 40A TP MCCB-5nos | 1 | No |  |  |
| 2.3 | APFC Panel |  |  |  |  |
| a | Incomer: |  |  |  |  |
|  | 250A TPN Isolator - 1 No |  |  |  |  |
|  | APFC Relay, MF Meter with CT & Indicators |  |  |  |  |
|  | 250A TPN Aluminium bus bar - 1 Set . |  |  |  |  |
| b | Outgoing: |  |  |  |  |
|  | 63A 4P MCB, 40A 3P Capacitor Duty Contactor with 20KVAR Heavy duty Capacitor - 2 No |  |  |  |  |
|  | 40A 4P MCB 25A 3P Capacitor Duty Contactor with 15KVAR Heavy duty Capacitor - 2 No |  |  |  |  |
|  | 32A 4P MCB, 16A 3P Capacitor Duty Contactor with 10 KVAR Heavy duty Capacitor - 2 No |  |  |  |  |
|  | 32A TPN SFU, 16A 3P Capacitor Duty Contactor with 5 KVAR Heavy duty Capacitor - 2 No | 1 | No |  |  |
| 3 | Supply and laying the following size of PVC APVC aluminium cable through existing trench / clamped on wall or ladder. |  |  |  |  |
| (a) | 3.5 x 120 Sqmm PVC APVC Aluminium cable. | 90 | Mtr |  |  |
| (b) | 3.5 x 185 Sqmm PVC APVC Aluminium cable. | 150 | Mtr |  |  |
| 4 | Supply and termination for the following size of PVC APVC aluminium cable using cable gland and socket. |  |  |  |  |
| (a) | 3.5 x 120 Sqmm PVC APVC Aluminium cable. | 6 | Nos |  |  |
| (b) | 3.5 x 185 Sqmm PVC APVC Aluminium cable. | 4 | Nos |  |  |
| 5 | Earthing |  |  |  |  |
| 5.1 | Supply and installation of Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. ,GI watering pipe of 25mm dia with funnel .The CI cover frame/ chamber shall be of 450mm x450mm size. | 4 | Nos |  |  |
|  | Providing and fixing 25 mmX3 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 30 | Mtr |  |  |
|  | Providing & fixing copper earth bus bar of section 50mm x 12.5mm thick, 1.2 meters long with brass bolts, nuts and copper washers on suitable epoxy resin cast bus bar insulators as required. | 2 | Nos |  |  |
| 5.2 | Supply and laying of 25 x 3mm copper strip for earthing: | 200 | Mtr |  |  |
| 6 | Supply, Fabrication & Erection of Vertical/Horizontal type M.S. Cable Trays. | 100 | Kg |  |  |
| 7 | Supply and Installation of 6KG Dry Chemical Powder |  |  |  |  |
|  | type (DCP) fire extinguishers having ISI mark |  |  |  |  |
|  | along with mounting supports. | 2 | Nos |  |  |
| 8 | Supply of Electrical ISI Grade Rubber Mat |  |  |  |  |
|  | suitable for 440Volts Switchboards. (6' x 3' x 1/4"). | 3 | Nos |  |  |
| 9 | Supply of Electrical ISI Grade Rubber Mat |  |  |  |  |
|  | suitable for 11000Volts Switchboards. (6' x 3' x 1/2"). | 2 | Nos |  |  |
| 10 | Fabrication ,supply, installationn of cable trenach covers using 6mm thick ms chequered plates of covering trenches in switch board room and substation | 4 | SqM |  |  |
| 11 | Supply of Electrical Grade rubber hand gloves |  |  |  |  |
| 12 | suitable for operation of 11KV Switchgear. | 1 | Set |  |  |
| 11 | Supply and installation of 2nos fire buckets along with |  |  |  |  |
|  | stand painted with enamel paint of red colour. | 2 | Nos |  |  |
| 12 | Supply and installation of L.T/H.T danger |  |  |  |  |
|  | sign boards. | 1 | No |  |  |
| 13 | Supply and installation of emergency OFF trip push |  |  |  |  |
|  | button with front Glass and painted in RED Colour. | 1 | No |  |  |
| 14 | Supply and installation of 1no 50/5 class 5P10 current Transformer with indoor type enclosure for standby Earth fault protection of 1no 250KVA indoor Transformer | 1 | No |  |  |
| 15 | Transporting the HT CT/PT units and TOD meter to the testing laboratories of KSEB and procuring approval for them. All expenses including transportation and miscellaneous expenses should be in the scope of the Contractor. | L.S |  |  |  |
| 16 | Preparation charges for getting approval and sanction from Electrical Inspectorate and KSEB excluding all liaison charges and statutory charges. | L.S |  |  |  |
| 17 | Transportation and shifting cost of 1 number 250 KVA Transformer from HLL Lifecare Ltd, corporate head office to Govt Medical College , Kozhikode. | L.S |  |  |  |
|  | Grant Total |  |  |  |  |