TENDER FOR DESIGN, FABRICATION, SUPPLY, ERECTION, VALIDATION & COMMISSIONING OF MICRO BIOLOGY LAB AT AKKULAM FACTORY, THIRUVANANTHAPURAM

IFB No: HLL/AFT/PROJECTS/2016-17/07/MICROLAB/05	                       DATE: 29.07.2016

##### HLL LIFECARE LIMITED

(A GOVT. OF INDIA ENTERPRISE)

AKKULAM FACTORY, SREEKARIYAM P.O.

THIRUVANANTHAPURAM – 695 017

Phone: +91 471 244 5930, Fax: +91 471 244 1383

Email: materialsaft@lifecarehll.com

Web: www.lifecarehll.com

##### HLL LIFECARE LIMITED

(A GOVT. OF INDIA ENTERPRISE)

AKKULAM FACTORY,  SREEKARIYAM P.O.,

THIRUVANANTHAPURAM – 695 017

IFB NO

DATE OF COMMENCEMENT 
OF SALE OF BIDDING DOCUMENT

LAST DATE FOR SALE OF BIDDING DOCUMENT

LAST DATE AND TIME FOR

RECEIPT OF BIDS

TIME AND DATE OF TECHNICAL OPENING OF BIDS

PLACE OF OPENING OF BIDS

ADDRESS FOR COMMUNICATION

:	HLL/AFT/PROJECTS/2016-17/07/MICROLAB/05  Dt. 29.07.2016

:	29.07.2016

:	22.08.2016, 14.30 HRS

:	22.08.2016, 15.00HRS

:	22.08.2016, 15.30 HRS

:	HLL LIFECARE LIMITED

AKKULAM  FACTORY,

SREEKARIYAM  P.O.

THIRUVANANTHAPURAM – 695017.

:	THE JOINT GENERAL MANAGER     (MATERIALS),

HLL LIFECARE LIMITED,

AKKULAM  FACTORY,

SREEKARIYAM  P.O.

THIRUVANANTHAPURAM – 695017

##### HLL LIFECARE LIMITED

(A GOVT. OF INDIA ENTERPRISE)

AKKULAM FACTORY, SREEKARIYAM P.O.

THIRUVANANTHAPURAM – 695 017

CONTENTS

| SECTION NO. | DESCRIPTION | PAGE NO. |
| --- | --- | --- |
| SECTION I | INVITATION FOR BIDDERS (IFB) | 3-7 |
| SECTION II | INSTRUCTION TO BIDDERS (ITB) | 8-21 |
| SECTION III | GENERAL CONDITIONS OF CONTRACT (GCC) | 22-33 |
| SECTION IV | SPECIAL CONDITIONS OF CONTRACT (SCC) | 34-46 |
| SECTION V | TECHNICAL SPECIFICATIONS | 47-64 |
| SECTION VI | GENERAL INFORMATIONS | 65 |
| SECTION VII | PERFORMANCE STATEMENT | 66-73 |
| SECTION VIII | FORMAT FOR REQUISITION FOR SITE VISIT | 74 |
| SECTION IX | PRICE SCHEDULE | 75-107 |
| SECTION X | CHECK LIST | 108-109 |
| SECTION XI | LAYOUT | 110 |

SECTION I

INVITATION FOR BIDS (IFB)

##### HLL LIFECARE LIMITED

(A GOVT. OF INDIA ENTERPRISE)

AKKULAM  FACTORY,

SREEKARIYAM  P.O.

THIRUVANANTHAPURAM – 695 017

INVITATION FOR BIDS (IFB)

IFB No.HLL/AFT/PROJECTS/2016-17/07/MICROLAB/05

Sealed and super scribed tenders under Two Bid systems are invited for the Design, Supply, Fabrication, Erection, Validation & Commissioning of Micro Biology Lab at HLL Lifecare Ltd, Akkulam Factory, Thiruvananthapuram

| S No | Name of the Item | EMD | Last Date& Time of Submission of Bids | Date & Time of Opening of Technical bids |
| --- | --- | --- | --- | --- |
| 1. | Tender for Design, Fabrication, Supply, Erection, and Validation & Commissioning of MICRO BIOLOGY LAB on turnkey basis at HLL Akkulam Factory. | Rs.1,00,000.00 in the form of DD from a scheduled bank payable at Thiruvananthapuram | 22nd AUGUST 2016 at 15.00 hrs | 22nd AUGUST 2016 at 15.30 hrs |

The detailed Tender Notice and tender documents can also be downloaded from our website www.lifecarehll.com. Amendments if any to this tender notice will be published only in HLL website.

JOINT GENERAL MANAGER (MATERIALS),

HLL LIFECARE LIMITED,

AKKULAM  FACTORY,

SREEKARIYAM  P.O.

THIRUVANANTHAPURAM - 695017

# Ph No: +91 471 2445930

# Fax No: +91 471 2445935

Email: materialsaft@lifecarehll.com

1. QUALIFICATION CRITERIA

- Minimum 3 years experience in the relevant field.

- Bidders should have constructed and installed at least 3 No. of similar clean rooms with individual values of at least Rs. 30 lakhs, during the past 3 years.

- The average annual turnover of the bidder should be above Rs. 75 Lakhs proven by balance sheet of three immediate previous financial years and they should produce proof for the same.

- It is mandatory that bidders must compulsorily visit the site and study the requirements before submitting the bid. Format for applying for site visit is as per attached Section– VIII. Copy shall be submitted along with the bid.

Note:-

- The bidder should furnish the information on past installations in the Pro-forma given under Section - VII.

- The bidder should furnish Registration Certificate and Certificate of        Incorporation.

- Bidders shall invariably furnish documentary evidence such as Completion certificate (Client’s Certificate) along with work order/Installation report in support of the satisfactory completion of the project as specified above.

- The Bidder shall furnish data to support that he has the financial and production capacity to perform the contract and complete the supplies within the stipulated delivery period.

- Latest solvency certificate obtained from a Scheduled Bank, for an amount not less than Rs 75 Lakhs.  The certificate is to be dated not earlier than one month from the date of submission of the tender.

- The bidder should furnish the copy of Audited balance sheet in proof of financial strength.

- Conditional Bid will be summarily rejected

2. 	 Interested eligible Bidders may obtain further information from the office of the

Joint General Manager (Materials), HLL Lifecare Ltd, Akkulam Factory, Thiruvananthapuram - 695017. (Phone No: 0471-2445930, email: materialsaft@lifecarehll.com  )

3.   A complete set of bidding documents may be purchased by any interested eligible bidder from the above office from 10.00 Hrs to 16.00 Hrs on any working day on submission of a written application to the above office and remitting a non- refundable fee of Rs. 2100 /- (including taxes) in the form of DD from a scheduled bank drawn in favor of HLL Lifecare Limited, payable at Thiruvananthapuram.

4.  The Tender Document can also be downloaded from our Website www.lifecarehll.com and cost of the Tender Document as mentioned above should be furnished in the form of Demand Draft from a scheduled bank in favor of M/s HLL Lifecare Limited payable at Thiruvananthapuram, along with Technical Bid. In case of non-submission of tender fee as DD from a scheduled bank along with bid, the bid shall be summarily rejected.

5 .     Interested eligible bidders may submit their bidding documents at the office of

the Joint General Manager (Materials), HLL Lifecare Ltd, Akkulam Factory,

Sreekariyam.P.O, Thiruvananthapuram –695 017 on or before the specified date and time.

6.   All bids must be accompanied by the items/documents specified herein and              must be delivered to the Joint General Manager (Materials) on or before 22.08.2016, 15.00 Hrs.  The bids (Technical Bids) will be opened on 22.08.2016 at 15.30 Hrs, in the presence of the bidders or their duly authorized personnel who wish to attend the bid opening on the specified date and time at HLL's office mentioned above. In the event of the date being declared a holiday for HLL, the due date for submission of bids and opening of bids will be the following working day at the same time.

7.      Completion Period:

The complete MICRO BIOLOGY LAB should be successfully constructed, validated and commissioned within 6 months from the date of issue of Purchase order/L.O.I.

No credit will be given for earlier deliveries/completion of work.

The Micro Biology Lab should be erected, validated, commissioned and handed over to Purchaser strictly within the time stipulated. The completion period quoted should be inclusive of the time taken by the Supplier for submission of fabrication drawings, if any, sufficient days for Purchaser’s approval/offering comments, sufficient notice to be given by Supplier for inspection/witnessing tests, time taken for booking of wagons, time taken for transportation to the site, fabrication, erection, testing, validation, commissioning and handling over of the installation completely ready for operation.

8.     Amendments

All amendments related to the tender shall be published only in HLL website www.lifecarehll.com

### SECTION II

INSTRUCTION TO BIDDERS

INSTRUCTION TO BIDDERS

INTRODUCTION

1. Eligible Bidders

The Eligibility criteria for the bidders is as per Qualification criteria stipulated in the tender document as per IFB clause -I.

2. Cost of Bidding

2.1 The Bidder shall bear all costs associated with the preparation and submission of its bid and HLL Lifecare Limited, Akkulam Factory, Thiruvananthapuram hereinafter referred to as “the Purchaser”, will in no case be responsible or liable for these  costs,  regardless  of  the  conduct  or  outcome  of  the  bidding process.

THE BIDDING DOCUMENTS

3. Contents of Bidding Documents

3.1 The goods required, bidding procedures and contract terms are prescribed in the Bidding documents. The Bidding documents include:

  - Invitation for Bids (IFB)

  - Instruction to Bidders (ITB)

  - General Conditions of Contract (GCC)

  - Special Conditions of Contract (SCC)

  - Technical Specifications

  - Performance statements

  - Declaration

  - Bid Form

  - Price Schedule

  - Check List

  - Contract form

3.2   The Bidder is expected to examine all instructions, forms, terms and specifications in the Bidding Documents. Failure to furnish all information required by the Bidding Documents or submission of a bid not substantially responsive to the Bidding Documents in every respect will be at the Bidder’s risk and may result in rejection of its bid.

4. CLARIFICATION OF BIDDING DOCUMENTS

4.1 A  prospective  Bidder  requiring  any  clarification  of  the  Bidding Documents may notify the Purchaser in writing at  the Purchaser’s mailing address indicated in the Invitation for Bids. The Purchaser will respond  to  any  request  for  clarification  of  the  Bidding Documents which it receives not later than 5 days prior to the deadline for submission of bids prescribed by the Purchaser. Purchaser’s response (including an explanation of the query but without identifying the source of inquiry) will be communicated through our web site / email to all prospective Bidders who have received the bidding documents.

5. AMENDMENT OF BIDDING DOCUMENTS

5.1 At any time prior to the deadline for submission of bids, the Purchaser may, for any reason, whether at its own initiative or in response to a clarification requested by a prospective bidder, modify the Bidding Documents by an amendment.

5.2 Any subsequent amendments in the bid shall be notified only on HLL website.

5.3 In order to allow prospective bidders reasonable time in which to take the amendment into account in preparing their bid, the Purchaser may, at its discretion, extend the deadline for the submission of bids

PREPARATION OF BIDS

6. Language of Bid

6.1 	The Bid prepared by the bidder and all correspondence and documents relating to the bid exchanged by the Bidder and the Purchaser, shall be 
written in the English language. Supporting documents and printed 
literature furnished by the Bidder may be written in another language 
provided; they are to be accompanied by an accurate translation of the 
relevant passages in the English language in which case, for purposes 
of interpretation of the Bid, the English translation shall govern

7. DOCUMENTS COMPRISING THE BID

Following documents and forms are to be included in the technical bid and commercial bid respectively.

7.1 TECHNICAL

The technical bid shall consist of the following documents.

- EMD / Bid Security amount in the form of DD from a scheduled bank, drawn in favor of HLL Lifecare Limited, payable at Thiruvananthapuram. The EMD / Bid Security shall be refunded to the non-responsive bidders within 60 days from the date of opening of Bid.

- The tender document cost in the form of DD from a scheduled bank, if the document is downloaded from HLL website.

- The technical specifications enclosed along with the bid document shall be confirmed by signature of the bidder/authorized signatory of the bidding firm, in all pages and authorized by official seal. All information requested in the specifications, dimensional drawings, technical literature describing the make offered, material etc., as specified

- Duly attested copies of sales tax registration, and documents to prove the legal status, place of registration and principal place of business of the undertaking.

- Copy of Balance sheet for the past three financial years, duly certified by a chartered accountant

- Performance statement in the pro-forma under section VII

- Documentary evidence established in accordance with Qualification criteria that the Bidder is eligible to bid and is qualified to perform the contract if the bid is accepted;

- Documentary evidence established in accordance with ITB Clause 11 that the equipment and ancillary services to be supplied by the Bidder shall conform to the Bidding Documents

- Duly filled Check list as per section XI

- All commercial aspects related to items that are mentioned in IFB

7.2 PRICE BID

a) Duly filled Bid Form as per section IX

b) Price schedule as per price abstract, sections IX (a) & (b) respectively.

8. BID PRICES

8.1 The bid is invited for “Design, Fabrication, Supply, Erection, Validation and Commissioning of MICROBIOLOGY LAB” as per the specifications, Terms & Conditions as specified in the Bid Documents etc. The bidder shall give the price separately for supply and installation as per the format in PRICE ABSTACT,  SECTION IX (A) & (B), PRICE SCHEDULE . The offer shall be firm in Indian Rupees.

8.2  Bidders shall have registration under Kerala VAT and shall produce necessary certificate from Kerala VAT authority for  deduction at specified rate / non deduction of WCT, if any applicable under Kerala VAT.  In case the bidder do not have Kerala VAT registration WCT @ 10% as per Kerala VAT rules will be deducted from total contract value.

8.3 Bidder shall supply the materials with applicable CST /VAT etc and no “C” Form shall be issued by HLL against supplies.

  - Bidder shall provide Excise Invoice (manufacturer invoice / dealer invoice) for excisable goods under supply schedule.

8.5  The price quoted by the bidder shall remain firm during the entire period of contract and shall not be subject to variation on any account. A bid submitted with an adjustable price quotation will be treated as non - responsive and rejected.

8.6   The prices quoted by the bidder shall be in sufficient detail to enable the Purchaser

to arrive at the price of equipment/system offered.

9. BID CURRENCIES

9.1 Bidders should quote in INR only.

10. DOCUMENTS ESTABLISHING BIDDER’S ELIGIBILITY AND QUALIFICATIONS

10.1   The bidder shall furnish, as part of its bid, documents establishing the bidder’s eligibility to bid and its qualifications, to perform the Contract if its bid is accepted.

10.2 The documentary evidence of the Bidder’s qualifications to perform the contract if                                                            the bid is accepted, shall be established to the Purchaser’s satisfactions. The bidder should have the financial, technical and production capability necessary to perform the Contract and meets the criteria outlined in the qualification requirements specified in the tender. To this end, all bids submitted shall include the following information:

(a) The legal status, place of registration and principle place of business of the company or firm or partnership, etc;

(b) Details of experience and past performance of the bidder on items offered and on those of similar nature within the past five years and details of current contracts in hand and other commitments as per proforma given in Section VII.

11. Documents establishing equipment and its parts and accessories conformity to bidding documents

11.1 Pursuant to ITB Clause10, the Bidder shall furnish, as part of its bid, documents establishing the conformity to the bidding documents of all goods and services which the bidder proposes to supply under the contract.

11.2 The documentary evidence of conformity of the equipment and its parts and accessories and services to the bidding documents may be in the form of literature, drawings and data and shall consist of:

(a) A detailed description of the essential technical and performance characteristics of the MICROBIOLOGY LAB;

(c)  An item-by-item commentary on the Purchaser’s Technical compliance demonstrating substantial responsiveness of the equipment and services to those specifications or a statement of deviations and exceptions to the provisions of the Technical Specifications.

11.3  For the purpose of the commentary to be furnished pursuant to ITB Clause11.2 (c)  above,  the  Bidder  shall  note  that  standards  for workmanship, material and equipments and references to brand names or  catalogue  numbers,  if  any,  designated  by  the  Purchaser  in  its Technical Specifications are intended to be descriptive only and not restrictive.

12. Period of Validity of Bids

12.1 Technical Bid & Price Bid shall be valid for minimum 120 days from the date opening of technical bid.

12.2 	In exceptional circumstances, the Purchaser may solicit the bidders consent to an extension of the period of validity. The request and the responses thereto shall be made in writing.

13. Format and Signing of Bid

13.1 The bidder shall prepare one copy of the BID.

13.2 The bid shall be typed or written in indelible ink and shall be signed by the Bidder or a person or persons duly authorized to bind the Bidder to the Contract. The letter of authorization shall be indicated by written power-of-attorney accompanying the bid. All pages of the bid, except for unamended printed literature, shall be initialed by the person or persons signing the bid.

13.3 Any interlineations, erasures or overwriting shall be valid only if they are initialed by the person or persons signing the bid.

14. Sealing and Marking of bids

Separate bids shall be submitted for price bid and technical bids.

14.1 The bidders shall seal Technical bid and Price bid in separate inner envelopes, duly marking the envelopes as COVER A -“TECHNICAL BID” and COVER B-‘PRICE BID. The Bidders shall then place both the inner envelopes in an outer envelope. The name of the project for which the bid is made must be written on both the inner envelops and the outer envelop.

14.2     The inner and outer envelopes shall be addressed to the Purchaser at  the following address:

Joint General Manager (Materials),

HLL Lifecare Limited,

Akkulam Factory,

Sreekariyam P.O,

Thiruvananthapuram –695017

(a) The outer envelope shall bear the Invitation for bids (IFB) number, 
and a statement: “DO NOT OPEN BEFORE” 15.00 Hrs. on  22.08.2016

(b)  The outer and inner envelope shall also indicate the name and address of the bidder to enable the bid to be returned unopened in case it is declared “late”.

(c)   If the inner and outer envelopes are not sealed and marked as required, the Purchaser will assume no responsibility for the bid’s misplacement or premature opening.

(d) Bids must be received by the Purchaser at the address specified not later than the date and time specified in the Invitation for Bids.   In the event of the specified date for the submission of bids, being declared a holiday for the Purchaser, the bids will be received up to the appointed time on the next working day.

(e) The Purchaser may, at its discretion, extend this deadline for the submission of bids by amending the bidding documents in which case all 
rights and obligations of the Purchaser and bidders previously subject to 
the deadline will thereafter be subject to the deadline as extended.

15. LATE BIDS

Any bid received by the Purchaser after the deadline for submission of  bids  prescribed  by  the  Purchaser,  will  be  rejected  and  returned  unopened to the bidder.

16.  MODIFICATION AND WITHDRAWAL OF BIDS

16.1 The bidder may modify or withdraw its bid after the bid submission, provided that written notice of the modification or withdrawal is received by the Purchaser prior to the deadline prescribed for submission of bids.

16.2 The bidder’s modification or withdrawal notice shall be prepared, sealed, marked and dispatched in accordance with the provisions of ITB Clause 15. A withdrawal notice may also be sent by fax or email but followed by a signed confirmation copy, post-marked not later than the deadline for submission of bids.

16.3 No bid may be modified subsequent to the deadline for submission of bids.

16.4 No bid may be withdrawn in the interval between the deadline for submission of bids and the expiration of the period of bid validity specified by the bidder in the Bid Document.

17. Opening of Bids by Purchaser

17.1 The Purchaser will open all the technical bids, in the presence of bidder's representatives who choose to attend, at 15.30 Hrs on 22.08.2016.

17.2 The bidder’s representatives who are present shall sign a register evidencing their attendance. In the event of the specified date of bid opening being declared a holiday for the Purchaser, the bids shall be opened at the appointed time and location on the next working day.

17.3 The bidder’s names, modifications, bid withdrawals and the presence or absence of the requisite documents and such other details as the Purchaser, at its discretion, may consider appropriate will be announced at the opening. No bid shall be rejected at bid opening, except for late bids, which shall be returned unopened to the bidder pursuant to ITB   Clause 16.

17.4   The Purchaser will prepare minutes of the bid opening

17.5 The “Price Bid” (Cover B) will be opened after evaluation of “Technical  bids” (Cover A) and the date and time of opening of price bid will be intimated to bidders whose bids are responsive and qualified by the Purchaser.

17.6 The purchaser will scrutinize the technical bid for compliance to the specifications and documentation requirement as per the bid document.  Purchaser will depute its competent officers to the premises of the bidders qualified on the basis of technical scrutiny, for on-site evaluation of the claims made in the technical bid, if deemed appropriate on purchaser’s sole discretion.  The  bidders  will  be  short-listed  on  the  basis  of responsiveness of technical bid as well as report of on-site technical  evaluation. The price bid of the bidders who are disqualified at the technical scrutiny and on-site evaluation will be returned un-opened. The on-site evaluation may include the inspection of the specimen model of the equipment. The short listed bidders will be informed about the time, date and venue of the price bid opening. The successful bidder shall be identified on the basis of lowest evaluated substantially responsive bid.

18.  CLARIFICATION OF BIDS

18.1 During evaluation of bids, the Purchaser may, at its discretion, ask the bidder for a clarification of its bid. The request for clarification and the response shall be in writing and no change in prices or substance of the bid shall be sought, offered or permitted.

18.2 Given specification is indicative only. The bidder should visit the plant and enquire about the items and also make their own assessments before quoting of bids. Prior permission from HLL shall be taken for visiting the plant. No photographs will be allowed inside the plant. The purchaser will not be responsible for any wrong quotes due to inadequate information.

19.    PRELIMINARY EXAMINATION

19.1   The Purchaser will examine the bids to determine whether they are complete, whether any computational errors have been made, whether the documents have been properly signed, and whether the bids are generally in order.

19.2 Arithmetical errors will be rectified on the following basis. If there is a discrepancy between the unit price and the total price that is obtained by multiplying the unit price and quantity, the unit price shall prevail and the total price shall be corrected. If there is a discrepancy between words and figures, the amount in words will prevail. If the bidder does not accept the correction of the errors, its bid will be rejected.

19.3 The Purchaser may waive any minor informality or non-conformity or irregularity in a bid, which does not constitute a material deviation, provided such a waiver does not prejudice or affect the relative ranking of   any bidder.

19.4   The purchaser will determine the substantial responsiveness of each bid to the bidding documents. For purposes of these clauses a substantially responsive bid is one which conforms to all the terms and conditions of the bidding documents without material deviations. Deviations from or objections or reservations to critical provisions such as those concerning Warranty, Force Majeure, Applicable law  and Taxes and Duties will be deemed to be material deviation. The purchaser’s determination of a bid’s responsiveness is to be based on the contents of the bid itself without recourse to extrinsic evidence.

19.5    If a bid is not substantially responsive, it will be rejected by the Purchaser and  may  not  subsequently  be  made  responsive  by  the  bidder  by correction of the non-conformity.

20. CONTACTING THE PURCHASER

20.1 No bidder shall contact the Purchaser on any matter relating to its bid, from the time of the bid opening to the time the contract is awarded. If the bidder wishes to bring additional information to the notice of the purchaser it should do so in writing.

20.2 Any effort by a bidder to influence the purchaser in its decisions on bid evaluation, bid comparison, or selection may result in the rejection of the bidders bid.

21. POST QUALIFICATION

21.1 The determination will take into account the bidders financial, technical and production capabilities. It will be based upon an examination of the documentary evidence of the bidder’s qualifications submitted by the bidder, pursuant to ITB Clause 12 as well as such other information as the Purchaser deems necessary and appropriate.

21.2 An affirmative determination will be a prerequisite for award of the contract to the bidder. A negative determination will result in rejection of the bidders bid, in which event the Purchaser will proceed to the next lowest evaluated bid to make a similar determination of that bidder’s capabilities to perform satisfactorily.

22. AWARD CRITERIA

22.1 Subject to ITB Clause 27, the Purchaser will award the contract to the successful bidder whose bid has been determined to be substantially responsive and has been determined as the lowest evaluated bid,  provided further that the bidder is determined to be qualified to perform the contract satisfactorily.

23. PURCHASER’S RIGHT TO ACCEPT ANY BID AND TO REJECT ANY OR ALL BIDS

23.1 The Purchaser reserves the right to accept or reject any bid, and to annul the bidding process and reject all bids at any time prior to award of Contract, without thereby incurring any liability to the affected bidder or bidders.

24. NOTIFICATION OF AWARD

24.1 Prior to the expiration of the period of bid validity, the Purchaser will notify the successful bidder in writing by registered letter or by fax or email to be confirmed, that its bid had been accepted.

24.2 The notification of award will constitute the formation of the contract

25. SIGNING OF CONTRACT AGREEMENT

25.1 The successful bidder has to sign a supply agreement on Kerala stamp paper worth Rs 100.00 the draft of which will be sent to the lowest responsive bidder, with a letter informing acceptance of bid. Within 21 days of receipt of the information regarding acceptance of the bid, the successful bidder shall sign the supply agreement and return it to the Purchaser.

25.2 Upon the successful Bidder’s furnishing of Security Deposit, the Purchaser will discharge EMD submitted by unsuccessful bidders.

- SECURITY DEPOSIT

  - Simultaneously with the execution of the contract, successful bidder within 15 days of the receipt of notification of award shall furnish a Security Deposit in the form of a Demand Draft from a scheduled bank drawn in favour of HLL Lifecare limited payable at Thiruvananthapuram or a Bank Guarantee from a scheduled bank, for an amount equal to 5% of the total contract value as Security Deposit for his faithful execution of contract. The Security deposit should be valid until successful completion of the contract and acceptance of the project by the Purchaser and will be released after acceptance of the project by the Purchaser and against submission of Performance Guarantee in the form of cash deposit or bank guarantee by the Supplier. In case of a delay in the works the validity of security deposit shall be extended.

26.2	  Failure of the successful Bidder to accept the notification of award or submission of security deposit within the timeframe shall constitute sufficient grounds for the annulment of the award and forfeiture of the EMD, in which even the Purchaser may make the award to the next lowest evaluated bidder or call for new bids.

27. Delays in Design, Manufacture, Supply, Installation, Validation and Commissioning of MICROBIOLOGY LAB

27.1 Delivery, Installation, Validation and Commissioning of the equipment and its parts and accessories shall be made by the Supplier within the stipulated delivery date as specified in the purchase order / work order / contract, from the date of placing the date of Order. If at any time during performance of the Contract, the Supplier should encounter conditions impeding timely Delivery, Installation, Validation and Commissioning of the MICROBIOLOGY LAB, the Supplier shall promptly notify the Purchaser in writing of the fact of the delay, its likely duration and its cause(s). As soon as practicable after receipt of the Supplier's notice, the Purchaser shall evaluate the situation and may at its discretion extend the Supplier's time for performance, with or without penalty.

27.2 A delay by the Supplier in the performance of its Delivery, Installation, Validation and Commissioning obligations shall render the Supplier liable to the imposition of penalty pursuant to agreement, unless an extension of time is agreed upon pursuant to agreement without the application of liquidated damages.

  - If the Supplier fails to deliver any or all of the equipment or its parts or perform the Services within the time period(s) specified in the Purchase Order, the purchaser shall, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as Liquidated Damages, a sum equivalent to the percentage specified in the purchase order.

- PAYMENT TERMS

28.1 Payment terms is as follows

28.1.1 Payment terms for supply

- 30% advance payment shall be released against BG (Bank Guarantee) from a scheduled bank valid  for a period of One year or till completion of Design, Manufacture, Supply, Installation, Validation and Commissioning of MICROBIOLOGY LAB .

- 40% of the payment shall be released within 15 days, against receipt of goods at HLL site and certified  by HLL Officials, based on actual quantities. Pro-rata payment can also be effected based on actual quantities received and certified by HLL  Officials.

- 20% of the payment shall be released after Installation, Commissioning and acceptance by HLL Officials

- Balance 10% will be retained as Retention Money which shall be released only after one year from the date of taking over the site or against a Performance Bank Guarantee from a scheduled bank for an amount equivalent to 10% value  of supply part, valid for a period of one year (warranty period) from the date of the issue of final “Project completion and acceptance certificate”, issued by HLL.

28.1.2 Payment terms for Installation

- 100% of the installation charges on satisfactory installation and commissioning of the project certified by HLL Officials against a Performance Bank Guarantee for an amount equivalent to 10% value  of Installation part, valid for a period of one year (defect security period) from the date of the issue of final “Project completion and acceptance certificate” issued by HLL..

28.2 Test Reports (wherever applicable) are to be forwarded along with the original invoices.

28.3 Payment shall be made in Indian Rupee only.

28.4 All other Statutory levies, such as Taxes, duties, WCT, INCOME TAX, SERVICE TAX & PF, ESI etc of the work men will be deducted from bill, as applicable.

28.5 Purchaser will not entertain presentation of documents through Bank.

29. Completion period.

The successful bidder has to design, supply, manufacture, validate & commission the Equipment within 6 months from the date of issue of work order/Letter of Indent.

30. Forfeiture of EMD

30.1 Failure of the successful Bidder to accept the notification of award or submission of security deposit within the timeframe shall constitute sufficient grounds for the annulment of the award and forfeiture of the EMD, in which even the Purchaser may make the award to the next lowest evaluated bidder or call for new bids.

31.2 The EMD may be forfeited:

(a)	If a Bidder withdraws its bid during the period of bid validity specified by the Bidder on the Bidding Document; or

(b)	In case of the successful Bidder, if the Bidder fails:

(i)	to sign the Contract

(ii)	to furnish security deposit

###### SECTION III

###### GENERAL CONDITIONS OF CONTRACT

TABLE OF CLAUSES

| Sl No | Description | Page No. |
| --- | --- | --- |
| 1. | DEFINITIONS | 24 |
| 2. | APPLICATION | 24 |
| 3. | STANDARDS | 25 |
| 4. | USE OF CONTRACT DOCUMENTS AND INFORMATION | 25 |
| 5. | PATENT RIGHTS | 25 |
| 6. | INSPECTION AND TESTS | 25 |
| 7. | PACKING | 26 |
| 8. | DELIVERY AND DOCUMENTS | 26 |
| 9. | INSURANCE | 26 |
| 10. | INCIDENTAL SERVICES | 28 |
| 11. | WARRANTY | 29 |
| 12. | PERFORMANCE GUARANTEE | 29 |
| 13. | PRICES | 30 |
| 14. | CHANGE ORDERS | 30 |
| 15. | CONTRACT AMENDMENTS | 31 |
| 16. | ASSIGNMENT | 31 |
| 17. | SUBCONTRACTS | 31 |
| 18. | LIQUIDATED DAMAGES | 31 |
| 19. | TERMINATION BY DEFAULT | 31 |
| 20. | FORCE MAJEURE | 32 |
| 21. | TERMINATION FOR INSOLVENCY | 32 |
| 22. | RESOLUTION OF DISPUTES | 32 |
| 23. | GOVERNING LANGUAGE | 33 |
| 24. | APPLICABLE LAW | 33 |
| 25. | NOTICES | 33 |
| 26. | TAXES AND DUTIES | 33 |
| 27 | ESCALATION | 33 |

GENERAL CONDITIONS OF CONTRACT

1. DEFINITIONS

1.1 In this contract the following terms shall be interpreted as indicated:

(a) “The Contract” means the agreement entered into between the Purchaser and the Supplier as recorded in the Contract Form signed by the parties, including all the attachments and appendices thereto and all documents incorporated by reference therein;

(b) “The Contract Price” means the price payable to the Supplier under the Contract for the full and proper performance of its contractual obligations;

(c) “The Goods” means all the products, equipment, machinery, and/or other materials which the Supplier is required to supply to the Purchaser under the Contract;

(d) “Services” means services ancillary to the supply of the Goods, such as transportation and insurance, and other incidental services, such as installation, commissioning, provision of technical assistance, training and other obligations of the Supplier covered under the contract;

(e) “GCC” means the General Conditions of Contract contained in this 
section.

(f) “SCC” means the Special Conditions of Contract.

(g) “The Purchaser” means the Organization purchasing the Goods, as named in SCC;

(h) “The Supplier” means the individual or firm supplying the Goods under this Contract;

(i) “Day” means calendar day.

(j) “Delivery period” means the period applicable up to the completion of supply; installation and testing by the supplier at the required location mentioned in purchase order and accepted by the Purchaser.

2. APPLICATION

2.1 These General Conditions shall apply to the extent that they are not superseded by provisions in other parts of the Contract.

3. STANDARDS

The Goods supplied under this Contract shall conform to the standards mentioned in the Technical Specifications, and, when no applicable standard is mentioned, to the authoritative standard appropriate to the Goods’ country of origin and such standards shall be the latest issued by the concerned institution.

4. USE OF CONTRACT DOCUMENTS AND INFORMATION

4.1 The Supplier shall not, without the Purchaser’s prior written consent, disclose the Contract, or any provision thereof, or any specification, plan, drawing, pattern, sample or information furnished by or on behalf of the Purchaser in connection therewith, to any person other than a person employed by the Supplier in performance of the Contract. Disclosure to any such employed person shall be made in confidence and shall extend only as far as may be necessary for purposes of such performance.

4.2 The Supplier shall not, without the Purchaser’s prior written consent, make use of any document or information enumerated in GCC Clause 4.1 except for purposes of performing the Contract.

4.3 Any document, other than the Contract itself, enumerated in GCC clause 4.1 shall remain the property of the Purchaser and shall be returned (in all copies) to the Purchaser on completion of the supplier’s performance under the Contract if so required by the Purchaser.

5. PATENT RIGHTS

The Supplier shall indemnify the Purchaser against all third-party claims of infringement of patent, trademark or industrial design rights arising from use of the Goods or any part thereof in India.

6. INSPECTION AND TESTS

6.1 The Purchaser or its representative shall have the right to inspect and/or to test the Goods to confirm their conformity to the Contract at no extra cost of the Purchaser. The Special conditions of Contract and/or the Technical Specifications shall specify what inspections and tests the Purchaser requires and where they are to be conducted. The Purchaser shall notify the Supplier in writing of the identity of any representatives retained for these purposes.

6.2 The inspections and test may be conducted on the premises of the Supplier or its subcontractor(s), at point of delivery and/or at the Goods final destination. Where conducted on the premises of the Supplier or its subcontractor(s),  all  reasonable  facilities  and  assistance  including access to drawings and production data - shall be furnished to the inspectors at no charge to the Purchaser.

  - Should  any  inspected  or  tested  Goods  fail  to  conform  to  the specifications, the Purchaser may reject them and the Supplier shall either replace the rejected Goods or make all alternations necessary to meet specification requirements free of cost to the Purchaser.

  - The Purchasers right to inspect, test and, where necessary, reject the Goods’ arrival in at site shall in no way be limited or waived by reason of the Goods having previously been inspected, tested and passed by the Purchaser or its representative prior to the Goods dispatched.

7. PACKING

7.1 The Supplier shall provide such packing of the Goods as is required to  prevent  their  damage  or  deterioration  during  transit  to  their  final  destination as indicated in the Contract. The packing shall be sufficient to withstand, without limitation, rough handling during transit and exposure to extreme temperatures, salt and precipitation during transit and open storage. Packing case size and weights shall take into consideration, where appropriate, the remoteness of the Goods final destination and the absence of heavy handling facilities at all points in transit.

7.2 The packing, marking and documentation, within and outside, shall comply strictly with such special requirements as shall be provided in the agreement / purchase order including additional requirements, if any, specified in SCC and in any subsequent instructions ordered by the Purchaser.

8 DELIVERY AND DOCUMENTS

Delivery, Installation, Testing and Commissioning of the MICRO BIOLOGY LAB shall be made by the Supplier in accordance with the terms specified in the purchase order by the Purchaser. The details of dispatching and/or other documents to be furnished by the supplier are specified in the purchase order, if any.

9. INSURANCE

The Supplier shall at his own expense carry and maintain insurance with reputed insurance companies to the satisfaction of the Purchaser as under:

i) Insurance of works:

The Supplier shall take full responsibility for loss, damage and care of plant and works until it is delivered to site, constructed, erected, commissioned and taken over by Purchaser. Without limiting such responsibility, the supplier shall in the interest of the work insure the plant and work for their full value plus ten percent until they have been taken over. Such insurance shall cover the equipments and works against loss, damage or destruction   by fire, earthquake, theft or any other cause, throughout the duration of the contract period or extended contract period.

ii) Insurance of employees:

The Supplier   shall   accept full and exclusive liability for the compliance of all obligations and responsibilities imposed by the Employees State Insurance Act, 1948 and its amendments and any liability or penalty which may be imposed by the Central, State or Local Authorities due to the reason of violation by the supplier or sub-supplier of the Employees State Insurance Act, 1948 and its amendments. The Supplier shall agree to fulfil the requirement of the Employees State Insurance Corporation and maintain the declaration forms and all such forms, which may be, required in respect of the supplier’s, sub-supplier's employees who are employed in the work provided for or those covered by   E.S.I.C. from time to time under the agreement. The Purchaser shall retain such sum as may be necessary from the total contract value until the supplier shall furnish satisfactory proof that all contributions as required by the Employees State Insurance Act, 1948 and its amendments have been paid by him.

iii) Workmen's Compensation:

Insurance shall be affected for all the Supplier’s employees engaged for this contract. The Supplier shall also carry and maintain all other insurance, which may be required under any   law or regulations from time to time. He should also carry and maintain any other insurance, which may be required by the Purchaser.

iv) Transit Insurance:

The cost of transit insurance relating to the items to be transported by the supplier to the site of work shall be borne by the supplier and the quoted price shall be inclusive of this cost.

v) Loss or damage and Indemnity Agreement:

The supplier shall be responsible during the progress of work as well as guarantee period for any liability imposed by law for any damage to work or any part thereof or to any of the material or other things including those of Purchaser used in performing the work or for injury to any person or persons or for any property damaged in or outside the site. The supplier shall indemnify and hold the Purchaser harmless against all liabilities, claims, loss or injury, including costs, expenses and attorney's fees incurred in the defence of same, arising from any allegation   whether groundless or not, of damage or injury to any person or property resulting from the performance of the work or from any material used in the work or from any condition of the work or work site or from any cause whatsoever during the progress and maintenance of the work.

vi) Third party insurance:

Before commencing the execution of the   works the Supplier, but without    limiting his obligations and responsibilities, shall insure against his liability for any material or physical damage, loss or injury which may occur to any property, including that of the Purchaser, or to any person, including any representative of the Purchaser, by or arising out of the execution of works or in the work being carried out by the Purchaser, by or arising out of the provision of clause 5 (v) here of. Such insurance shall be affected with an insurer and in terms approved by the Purchaser.

vii) The Supplier shall take Supplier’s All Risks Insurance policy, jointly in the name of HLL Lifecare Limited and the Supplier and the insurance should be valid till the satisfactory completion of the work.  The copy of the policy shall be deposited with HLL before commencing the work.

10.  INCIDENTAL SERVICES

The supplier may be required to provide any or all of the following services, including additional services, if any, specified in SCC:

(a) Performance or supervision of the on-site assembly and/or start-up of the supplied goods

(b) Furnishing of tools required for assembly and/or maintenance of the supplied goods;

(c) Furnishing of detailed operations and maintenance manual

(d) performance or supervision or maintenance and/or repair of the supplied Goods, for a period of time agreed by the parties, provided that this service shall not relieve the Supplier of any warranty obligations under this Contract; and

(e) Training of the Purchaser’s Personnel, at the Supplier’s plant and/or on-site, in assembly, start-up, operation, maintenance and/or repair of the supplied Goods.

11. WARRANTY

11.1 The Supplier warrants that the Goods supplied under this Contract are of the most recent or current models and incorporate all recent improvements in design and materials unless provided otherwise in the Contract. The supplier further warrants that the Goods supplied under this Contract shall have no defect arising from design, materials or workmanship (except when the design and/or material is required by the Purchaser’s specifications) or from any act or omission of the Supplier, that may develop under normal use of the supplied Goods in conditions obtaining in the country of final destination

11.2 This warranty shall remain valid for minimum ONE YEAR, as applicable, after the Goods and services or any portion thereof  as  the  case may  be,  have  been  delivered  to  and accepted/ installed & commissioned at the final destination indicated in the Contract.

11.3   The Purchaser shall promptly notify the supplier in writing of any claims arising under this warranty.

11.4   Upon  receipt  of  such  notice,  the  Supplier  shall,  within  the  period specified in SCC, and with all reasonable speed, repair or replace the defective Goods or parts thereof, without cost to the Purchaser

11.5   If the Supplier, having been notified, fails to remedy the defect(s) within the period specified in SCC, within a reasonable period, the Purchaser may proceed to take such remedial action as may be necessary, at the Supplier’s risk and expense and without prejudice to any other rights which the Purchaser may have against the Supplier under the contract.

11.6 Manufacturers warranty of the equipment/electrical items, if any shall be passed on to HLL

12. PERFORMANCE GUARANTEE

The Supplier shall fully guarantee that all the equipment supplied will perform in accordance with the specifications and will be free of all defects in design, material and workmanship. Should any equipment not performing as intended or should the design, material or workmanship prove defective within guarantee period the equipment shall, upon notification of deficiency or defect, be promptly corrected by the Supplier to the satisfaction of Purchaser without delay and at no extra cost.  If the Supplier fails to take proper corrective action to replace or repair the deficiency within a reasonable time of Purchaser’s notification to this effect, the Purchaser shall be free to take such corrective action at the Supplier’s risk and cost.

Even if Inspection and/or tests are fully carried out by Purchaser or their representatives, the Supplier is not absolved to any degree of his responsibility to ensure that all equipment and materials supplied comply strictly with the requirements as per specifications given in the order, and the Purchaser shall be free to point out any defect till the guarantee period is over.

Simultaneously with the successful completion of the contract, supplier shall furnish a Performance guarantee in the form of a Demand Draft from a scheduled bank or a Bank Guarantee in the HLL’s prescribed format from a scheduled bank or from balance payment to be paid to the supplier as per contract, acceptable to the purchaser, for an amount equal to 10% of the total price on the value of the contract as Deposit for his faithful execution of Performance Guarantee. The Performance guarantee should be valid for the Guarantee Period.

13. PRICES

13.1 Prices charged by the Supplier for Goods delivered and Services performed under the Contract shall not vary from the prices quoted by the Supplier in its bid, with the exception of any prices adjustments authorized in the special Conditions of Contract or in the Purchaser’s request for bid validity extensions, as the case may be.

14. CHANGE ORDERS

14.1 The Purchaser may at any time by written order given to the Supplier, make changes within the general scope of the Contract in any one or more of the following:

(a) drawings, designs or specifications, where Goods to be furnished  under  the Contract are to be specifically manufactured for the Purchaser;

(b) the method of shipping or packing

(c) the services to be provided by the Supplier.

14.2 If any such changes cause an increase or decrease in the cost of, or the time required for, the Supplier’s performance of any provisions under the Contract, an equitable adjustment shall be made in the Contract Price or delivery schedule, or both, and the Contract shall accordingly be amended. Any claims by the Supplier for adjustment under this clause must be asserted within thirty (30) days from the date of the Supplier’s receipt of the Purchaser’s change order.

15. CONTRACT AMENDMENTS

Subject to GCC Clause 14, no variation in or modification of the terms of the Contract shall be made except by written amendment signed by the parties.

16. ASSIGNMENT

The Supplier shall not assign, in whole or in part, its obligations to perform under the contract, except with the Purchaser’s prior written consent.

17. SUBCONTRACTS

The supplier shall notify the Purchaser in writing of all subcontracts awarded under the contract if not already specified in his bid. Such notification, in his original bid or later, shall not relieve the Supplier from any liability or obligation under the contract.

18. LIQUIDATED DAMAGES

If the Supplier fails to deliver any or all of the Goods or to perform the Services within the period(s) specified in the Contract, the Purchaser shall, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as liquidated damages, a sum equivalent to the percentage specified in SCC, up to a maximum deduction of the percentage specified in the SCC if any. Once the maximum is reached, the Purchaser may consider termination of the Contract.

19. TERMINATION BY DEFAULT

19.1  The Purchaser may, without prejudice to any other remedy for breach of contract, by written notice of default sent to the supplier, terminate the Contract in whole or part;

(a) If the Supplier fails to deliver any or all of the goods within the time period(s) specified in the Contract, or within any extension thereof granted by the Purchaser, or

(b) If the Supplier fails to perform any other obligation(s) under the contract.

19.2  In the event the Purchaser terminates the Contract in whole or in part,  the Purchaser may procure, upon such terms and in such manner as it  deems appropriate, Goods or Services similar to those undelivered, and  the Supplier shall be liable to the Purchaser for any excess costs for  such  similar  Goods.  However,  the  Supplier  shall  continue  the  performance of the Contract to the extent not terminated.

20.  FORCE MAJEURE

20.1 For purposes of this Clause “Force Majeure” means an event beyond the control  of the Supplier and not involving the Supplier’s fault or negligence and not foreseeable. Such events may include, but are not limited to, acts of the Purchaser either in its sovereign or contractual capacity, wars or revolutions, fires, floods, epidemics, quarantine restrictions and freight embargoes.

20.2 If a Force Majeure situation arises, the Supplier shall promptly notify the Purchaser in writing of such conditions and the cause thereof. Unless 	otherwise directed by the Purchaser in writing, the Supplier shall continue to perform its obligations under the Contract as far as is reasonably practical, and shall seek all reasonable alternative means for performance not prevented by the force majeure event.

21. TERMINATION FOR INSOLVENCY

21.1 The Purchaser may at any time terminate the Contract by giving written notice to the Supplier, if the Supplier becomes bankrupt or otherwise insolvent. In this event, termination will be without compensation to the Supplier, provided that such termination will not prejudice or affect any right of action or remedy which has accrued or will accrue thereafter to the Purchaser.

22. RESOLUTION OF DISPUTES

22.1 The Purchaser and the supplier shall make every effort to resolve amicably by direct informal negotiation any disagreement or dispute arising between them under or in connection with the Contract.

If, after thirty (30) days from the commencement of such informal negotiations, the Purchaser and the Supplier have been unable to resolve amicably a Contract dispute, either party may require that the dispute be referred for resolution to the formal mechanisms specified in the Special Conditions of Contract. These mechanisms may include, but or not limited to, conciliation mediated by a third Party, adjudication in an agreed national forum, and national arbitration.

22.2 The jurisdiction of any disputes, suits and proceeding arising out of the tender shall be only in the court of Thiruvananthapuram.

23. GOVERNING LANGUAGE

The contract shall be written in English language. English language version of the Contract shall govern its interpretation. All correspondence and documents pertaining to the Contract which are exchanged by the parties shall be written in the same language.

24. APPLICABLE LAW

The Contract shall be interpreted in accordance with the laws of the Union of India.

25. NOTICES

25.1   Any notice given by one party to the other pursuant to this Contract shall be sent to other party in writing or by fax or email and confirmed in writing to the other Party’s address specified in Special Conditions of Contract

25.2   A notice shall be effective when delivered or on the notice’s effective date, whichever is later.

26. TAXES AND DUTIES

26.1 Suppliers shall be entirely responsible for all taxes, duties, license fees, octroi etc., incurred until Delivery, Installation, Testing and Commissioning of the contract to the Purchaser.

- ESCALATION

The rates quoted by the Supplier in the contract documents shall be final and shall not be subjected to any change due to the increase in labour wages or inflation in the cost of materials or any other price variations due to any reason during the stipulated time period of the contract or during the extended time period of completion.

SECTION IV

SPECIAL CONDITIONS OF CONTRACT

TABLE OF CLAUSES

| Sl No | Description | Page No. |
| --- | --- | --- |
| 1. | DEFINITIONS | 36 |
| 2. | INSPECTION AND TESTS | 36 |
| 3. | INSURANCE | 36 |
| 4. | INCIDENTAL SERVICES | 36 |
| 5. | WARRANTY | 36 |
| 6. | EARNEST MONEY DEPOSIT | 37 |
| 7. | PRICES | 37 |
| 8. | SUBCONTRACTS | 37 |
| 9. | LIQUIDATED DAMAGES | 38 |
| 10. | RESOLUTION OF DISPUTES | 38 |
| 11. | INSTALLATION, VALIDATION& COMMISSIONING | 38 |
| 12. | OPERATIONAL ACCEPTANCE | 39 |
| 13. | TRAINING | 39 |
| 14. | VARIATION IN DRAWING AND SPECIFICATIONS | 39 |
| 15. | FABRICATION SHEDULE | 39 |
| 16. | PROGRESS REPORT | 39 |
| 17. | STAFF AND WORJERS | 40 |
| 18. | CO-OPERATION WITH OTHER AGENCIES AT SITE | 40 |
| 19. | SAFETY OF ADJOINING PROPERTIES | 40 |
| 20. | EXECUTION OF WORK | 41 |
| 21. | LIABILITIES FOR DEFECTS AND RECTIFICATION | 42 |
| 22. | CARE OF WORKS | 42 |
| 23. | LABOUR LAWS AND SAFETY REGULATIONS | 42 |
| 24. | SAFETY CODE | 43 |
| 25. | DETAILS OF WORK EXECUTION | 44 |
| 26. | SUPPLIERS SCOPE OF SUPPLY | 45 |
| 27. | RECOVERY FROM THE SUPPLIER | 45 |
| 28. | SPECIAL INSTRUCTION | 45 |
| 29. | SECRECY | 46 |

SPECIAL CONDITIONS OF CONTRACT

The following Special Conditions of Contract shall supplement the General Conditions of Contract. Whenever there is a conflict, the provisions herein shall prevail over those in the General Conditions of contract. The Corresponding clause number of the General Conditions is indicated in parentheses.

1. DEFINITIONS (GCC Clause 1)

The Purchaser is HLL Lifecare Limited, Akkulam Factory, Thiruvananthapuram.

2. INSPECTION AND TESTS (GCC Clause 6)

2.1 The Purchaser or its representative shall inspect and/or test any or all the equipment to confirm their conformity to the Contract specifications, prior to dispatch from the manufacturer’s premises. Such inspection and clearance will not prejudice the right of the consignee to inspect and test the equipment on receipt at destination.

2.2 If the equipment fails to meet the laid down specifications the supplier shall take immediate steps to remedy the deficiency or replace the defective equipment/ parts to the satisfaction of the Purchaser.

3. INSURANCE (GCC Clause 9)

3.1 For delivery of materials at site, the insurance shall be obtained by the Supplier in an amount equal to 110% of the value of the equipment from “Warehouse to Warehouse” (Final destinations) on “All Risks” basis including War Risks and Strike if applicable.

4. INCIDENTAL SERVICE (GCC Clause 10)

4.1 The following services covered under GCC Clause 10 shall be furnished and the cost shall be included in the contract price:

(a) Transportation, safe storage and handling of consignment off site.

(b) On site assembly if any of the supplied equipment, installation, testing and

Commissioning of the equipment.

(c) Furnishing 3 No of detailed operations and maintenance manual for each

appropriate unit of supplied equipment;

5. WARRANTY (GCC Clause 11)

Substitute GCC Clause 11.2 by the following:-

5.1 This warranty shall remain valid for minimum ONE year after Installation, Validation and Commissioning and handing over of the MICROBIOLOGY LAB or any portion thereof as the case may be, have been accepted by HLL Lifecare Limited as indicated in the contract.

5.2 Any major repair pointed out by the Purchaser within the warranty period shall be rectified by the Supplier from the date of intimation within a period  of 3  calendar  days  and  commission  the  equipment  to  the satisfaction of the Purchaser. Failing which the Purchaser has the right to  levy  penalty on the basis of less incurred on  the  Supplier  per  day  or  part  thereof  for  the equipment until the equipment are repaired and commissioned to the satisfaction of the Purchaser.

5.3 The Supplier shall, in addition, comply with the performance and/ or consumption guarantees specified under the contract. If for reasons attributable to the Supplier, these guarantees are not attained in whole or in part, the Supplier shall at its discretion either:

Make such changes, modifications, and/or additions to the equipment or any part thereof as may be necessary in order to attain the contractual guarantees specified in the Contract at its own cost and expense and to carry out further performance tests in accordance with SCC 2:

6. Earnest Money deposit (EMD)

6.1 Technical Bid should accompany a DD  from a scheduled bank drawn in favour of M/s.HLL LIFECARE LIMITED, and payable at Thiruvananthapuram for a sum of Rs.1,00,000/- towards Earnest Money Deposit.   Failing which the Tender will be rejected.

6.2 E.M.D. from unsuccessful bidders will be returned after the acceptance of agreement / work order by the L1 party.

6.3 In the case of successful bidder, the Earnest Money will be returned after signing the contract, and submission of Security Deposit, which they will have to offer for the faithful execution of the contract.

7. PRICES (GCC Clause 13)

Substitute Clause 13.1 of the GCC with the following:

Prices payable to the Supplier as stated in the Contract shall not be subject to adjustment / variation during performance of the Contract.

8. SUB CONTRACT (GCC Clause 17)

Add at the end of sub-clause 17.1 the following:

Sub-contract shall be only for bought-out items and sub-assemblies.

9. LIQUIDATED DAMAGES (GCC Clause 18)

For delays: Substitute GCC Clause 18.1 by the following:

If the Supplier fails to deliver any or all of the equipment or perform of services  within  the  time  period(s)  specified  in  the  Contract,  the purchaser  shall  without  prejudice  to  its  other  remedies  under  the Contract, deduct from the Contract Price, as liquidated damages, a sum equivalent to 0.5 percent of the value of order per week of delay subject  to a maximum deduction of 5.0%.  Once the maximum is reached, the Purchaser may consider termination of the Contract.

10. RESOLUTION OF DISPUTES (GCC Clause 22)

Add as GCC Clauses 22.1 and 22.2 the following:

10.1 The dispute resolution mechanism to be applied pursuant to GCC Clause 22 shall be as follows:

(a)In the case of a dispute or difference arising between the Purchaser 
and a Supplier relating to any matter arising out of or connected with this 
agreement, such dispute or difference shall be settled in accordance 
with the Arbitration and Conciliation Act 1996 the Arbitral Tribunal shall 
consist of 3 Arbitrator, one each to be nominated by the Purchaser and 
the supplier. The third Arbitrator shall be chosen by the two Arbitrators 
so appointed by the parties and shall act as Presiding Arbitrator. In case 
of failure of the two Arbitrator appointed by the parties to reach upon a 
consensus with in a period of 30 days from the appointment of the 
Arbitrator  appointed  subsequently,  the  Presiding  Arbitrator  shall  be 
appointed by the President of Institute of Engineers (India).

10.2 The venue of arbitration shall be the place from where the Contract is issued (i.e.) Thiruvananthapuram

11.  INSTALLATION, VALIDATION & COMMISSIONING

Design, manufacture, Supply, installation, validation and commissioning of MICROBIOLOGY LAB shall be completed by the supplier in accordance with the terms and technical specifications made by the purchaser.

12.  OPERATIONAL ACCEPTANCE:

- Performance Test: The performance test shall be conducted by the supplier during the commissioning of the facilities to ascertain whether the facilities can attain the functional guarantees.

- Operational Acceptance: Operational Acceptance shall occur in respect of the facilities when the performance test has been successfully completed and the functional performances are met.

13. TRAINING

The bidder shall provide training for maintenance staff of the purchaser free of cost where required.

The bidder shall provide all training material and documents.

Conduct of training of the purchaser’s personnel shall be on-site.

- VARIATION IN DRAWINGS AND SPECIFICATIONS

The Purchaser has the right to change the drawings regarding dimensions but specification remaining the same. However such changes shall not entitle the supplier for any compensation, claim regarding the change in scope of work.

15. FABRICATION SCHEDULE

The Supplier shall furnish to Purchaser, a PERT/BAR CHART, within 7 days of receipt of the Order.  The PERT/BAR Chart, should give all important milestones such as ordering of material, completion of procurement, release of drawings, phased fabrication/manufacture, inspection/tests at Supplier’s works, despatch, start and completion of erection at site (wherever applicable) etc.  Purchaser has the right to depute their representative to the Supplier’s works to check his adherence to such chart. If any of the initial or intermediary milestones gets delayed for any reasons, the Supplier shall adjust the subsequent milestones in such a way that the final date for delivery/handing over of the equipment as per the Order is not affected.

- PROGRESS REPORT

During execution of the contract, the supplier shall furnish bi-weekly progress reports to the Purchaser indicating the progress achieved during the week and the total progress up to the last week as against scheduled and anticipated completion dates in respect of key phases of the work.  The Supplier shall also furnish   any other information in order to ascertain progress, if called for by the Purchaser.

- STAFF AND WORKERS

The supplier shall depute qualified engineers for execution of the project. The technical   staff employed by the supplier shall be responsible for the quality and workmanship of the work as per the satisfaction of the Purchaser. The Supplier’s supervisory staff should follow the instructions given by Purchaser /Consultant or his authorized representative. If any of the Supplier’s staff members is incapable or in-experienced, in the opinion of the Purchaser, then he should be removed immediately and the supplier should do suitable substitution.

If the workers or the supervising staff of the supplier are involved in riotous or illegal   activities to such an extent that it becomes necessary to hand over the matter to the police then the supplier would be solely responsible for the case and all the expenses incurred in the legal proceedings shall be borne by the supplier.

- CO-OPERATION WITH OTHER AGENCIES AT SITE

The Supplier or his authorized representatives must work in close co-operation with the agencies executing other works forming the part of the project and also with the representatives of the Purchaser for the execution of works which are not included in the contract. Supplier shall permit free access and generally afford reasonable facilities to other agencies or departmental workmen etc.

The Supplier’s quoted amount/rate shall be deemed to cater for all the above contingencies and nothing extra shall be admissible on this account.

Supplier should keep his working site clean and the materials brought for work shall be kept in a properly stacked / stored way. The work site should be swept at the end of each working day after removal of debris / left over materials. The Supplier has to take full care so as not to spoil or damage other Supplier's/ Purchaser’s job / material.

- SAFETY OF ADJOINING PROPERTIES

The Supplier or his authorised representatives should conduct all the operations necessary for the execution of works in such a manner that no inconvenience / damage is caused to the properties of other persons & Purchaser.

- EXECUTION OF WORK

General:

All the works shall be executed in accordance with the detailed drawings, specifications and instructions to be given by the Purchaser or mentioned in the contract document.

Drawings:

The drawings given in the tender document are only for reference purposes. The bidder has to inspect the site and submit the bid accordingly. The drawings given in the tender document are as per our present requirement. The supplier has to discuss with purchaser for the exact requirement to prepare the working drawing by him.

Inadequate/substandard works and materials:

i) If any material used by the Supplier is found unsuitable or of sub-standard quality after testing, then the Supplier shall remove those faulty materials immediately as per the instructions of the Purchaser.

ii) If any work executed by the Supplier is found to be of bad workmanship or not as per the drawings, then the same is to be dismantled and re-executed by the Supplier without claiming any extra payment or extension in time period.

Default of Supplier in compliance:

If the supplier or his authorized representative fails to follow the instructions given by the Purchaser regarding any of the works, then the same shall be got executed by other persons employed by the Purchaser and the expenses incurred shall be borne by the Supplier.

Discrepancies between instructions:

If any discrepancy occurs between the various instructions conveyed to Supplier or his authorized representative or if any misunderstanding arises between the Supplier’s staff and Purchaser's staff, the supplier shall report the matter immediately to the Purchaser. The decisions of Purchaser shall be final and binding. Moreover, no claims for losses due to discrepancies between instructions, doubts or misunderstandings shall be admissible.

Change in specifications:

If there is any variation in specification   or   any change in make of item, then it has got to be approved from the Purchaser prior to installation or execution.

Work not specified in the specification:

If, for any work, no specification has been given in the tender document, then the work will be executed as per the IS specifications, and if the work is not covered by IS specifications , then it should be executed as per standard engineering practice, subject to the approval of the Purchaser.

Work not specified with the scope:

If any work which is not mentioned in the scope but necessary for the successful completion of work, then it should be executed by the supplier without any additional amount.

- LIABILITIES FOR DEFECTS AND RECTIFICATIONS

If it shall appear to the Purchaser that any work has been executed with imperfect or unskilled workman or with materials of any inferior description, or of quality inferior to that contracted for, or otherwise not in accordance with the contract, the Supplier shall on demand in writing from the Purchaser or his representative specifying the work, materials or articles complained of, not withstanding that the same may have been inadvertently passed, certified and paid for, forthwith rectify or  remove and reconstruct  that work so specified and provide  other proper and suitable materials or articles at his own charges and cost, and in  the event of failure to do so within  a period to be specified by the Purchaser or his demand aforesaid,  the Purchaser may on expiry  of  notice period rectify or remove, re-execute the work at the risk of  Supplier and the  cost  shall  be recovered from   the Supplier. The decision of the Purchaser as to any question arising under this clause shall be final and conclusive.

- CARE OF WORKS

From the commencement to the completion of works, the Supplier shall take full responsibility for the care of all works including all temporary works and in case any damage or loss occurs then the supplier shall at his own cost repair and make good the same so that on completion of the work, the same shall be in good order in every respect in accordance with the contract and to the satisfaction of the Purchaser.

- LABOUR LAWS AND SAFETY REGULATIONS

Labour Laws:

i)   Labourers below the age of 18 years shall not be employed on the work.

ii)  The supplier shall not pay less than what is specified by the law to labourers engaged by him on the work.

iii) The supplier shall, at his own expenses, comply with all labour laws and the Purchaser shall not be responsible for any recovery/penalty imposed by the respective authorities for violating the labour laws.

iv) If the supplier is covered under the Contract Labour (Regulation & Abolition) Act, he shall obtain a license from the licensing authority (i.e. the Office   of Labour Commissioner), by payment of the necessary prescribed fee and deposit, if any, before starting the work.

v) The supplier shall furnish to the Purchaser, the details of the workers employed on the works.

vi) The supplier shall comply with the provisions of the existing rules and regulations relating to labour laws.

vii) The Purchaser shall on a report having been made by  an inspecting officer as defined in Contract Labour (Regulation  and Abolition) Act, 1980, have the power to deduct from  the amount  due to the supplier any sum required or  estimated   to be  required for making good the losses suffered by  a worker  or  workers by reason  of non-fulfillment of the conditions of the contract for the benefit of the workers, or if deductions made from his or their wages which are  not  justified by the terms of contract or non-observance of  the said regulations.

Minor Accident on Duty:

For cases of minor accident on duty not covered under compensation by insurance, the supplier shall have to compensate the affected person by reimbursing these medical expenses against submission   of   actual expenditure document. The absence from duty, if takes place, due to such accident shall be considered as special leave and full payment shall have to be made for duration of such absence.

Provident Fund:

It shall be solely the Supplier’s responsibility to complete all provident fund formalities as per statuary regulations.

- Safety CODE:

Safety and Protection:

The supplier shall adhere to safe construction practice and guard against hazardous and unsafe working conditions. While carrying out the work, the supplier should provide for;

i)   Safety of personnel engaged in the construction.

ii)  Protection and safety of works and materials during their progress.

iii) Sanitary and hygienic conditions of working and living for his workers, as required by the Purchaser.

Use of Safety Gadgets:

The Supplier shall have to ensure availability and use of all desire safety gadgets like safety shoes, belts, helmets, goggles, hand gloves etc.

Unsafe working condition:

If any activity is found to be progressing without proper and complete safety measures (including use of safety gadgets) being implemented, the supplier may be asked to stop the work unless he fulfils the desired safety norms. Such delays shall not be allowed to be considered for extension in duration of the allotted time period.

First Aid:

The supplier shall provide first aid facilities for his employees and those of his sub-SUPPLIERS. The requisite first aid box and medicines should always be available at work site.

Supplier's Barricades:

The supplier shall erect and maintain barricades required in connection with his

Operations to guard or protect: -

i)   Excavations

ii)  Hoisting Areas

iii) Areas adjudged hazardous by the Supplier's or Purchaser’s representatives.

iv) Charged electrical panels.

v)	 Purchaser’s existing property liable to get   damaged by supplier’s operation.

Preservation of peace:

The supplier shall take precautions to prevent any riotous or unlawful behaviour by his workers, for the preservation of peace and protection of inhabitants and the security of property in the neighbourhood of the work.

- DETAILS OF WORK EXECUTION

i) The work shall be done in such a manner so as to clear work front availability for other agencies working at site.

ii) Finish of work shall be as per drawings & details given by Purchaser.

iii) In general the complete work is to be done as per Indian Standard and esthetical norms as specified and detailed in Tender.

- SUPPLIER’S SCOPE OF SUPPLY

All materials required for executing the jobs specified in the Schedule of Items, inclusive of all tools, tackles, scaffolding, consumables & testing equipments shall be procured and supplied by the supplier at his own cost except for any items specified as Purchaser supplied.

- RECOVERY FROM THE SUPPLIER

i)	If the supplier or his employees damage or destroy the property of the Purchaser, then the same shall be replaced/refunded by the supplier; otherwise   the expenses may be recovered from his bill or security deposit.

ii) All compensation & recoveries to be made as per terms of the contract shall be deducted from the supplier's bill or security deposit.

iii) Forfeiture of Security Deposit:  If the supplier abandons the work or leaves the work incomplete, then the Purchaser has the right to forfeit the security deposit.

- SPECIAL INSTRUCTIONS

a) 	All materials to be used in execution of project shall be of first class quality; I.S.I. marked and shall be approved by Purchaser before its application.

b) The supplier shall be paying all testing charges required for testing of materials and samples as and when taken by Purchaser. The Supplier shall arrange necessary labour and transportation to facilitate testing of samples/materials. Frequency of testing materials/samples shall be as per related I.S. codes.

c) The work should be carried out in truly professional manner, neatly finished with proper line, level and plumb. Cleanliness and finishing of the job is of utmost importance. Hence the job should be done most carefully with best workmanship. For all finishing jobs samples should be approved from the purchaser/consultant before completely executing the work.

d) The Purchaser should be immediately informed for any discrepancy   in drawings, specifications and instructions in the execution of job, before actual execution of particular item having discrepancy.

e) Any item found to be having been executed with poor workmanship or materials of inferior quality then the supplier shall have to rectify /reconstruct the work as specified by Purchaser. No extra charge will be admissible in such case. If SUPPLIERS fails to do so, the Purchaser reserves the    right    to rectify/reconstruct the work through some other agency at the expenses of supplier.

f) The   schedule of activities as submitted by   the supplier shall have to be strictly adhered to. Regular progress reports shall have to be submitted by the supplier giving all details for monitoring of the schedule.

h)  Special care is to be taken for cleanliness of the site. After the end of day's work, the site should be cleaned immediately.

i)  The supplier shall have to co-operate with   the agencies executing other works in the same area.

j)  While executing the work, the supplier shall ensure safety and security of the property of the Purchaser so as to avoid theft etc.

- SECRECY

The purchaser is the sole owner of the technology, equipment specification and drawings given along with the bidding document and to be given to the supplier. The details given to bidders and supplier should be kept confidential and should not be used for any other purpose or should not be used or transferred to third party. The supplier has to sign a secrecy agreement with purchaser.

SECTION V

TECHNICAL SPECIFICATIONS

GENERAL

SCOPE OF WORK

- Double skin wall paneling and false ceiling with GI sheet and PUF insulation for Class 1000 clean room area

- GI Doors for Class 1000 area and comfort a/c area

- Air conditioning system with DX chillers, ducting, terminal filters and other accessories for class 1000 clean room area

- Complete Electrical work with light accessories and fire detectors inside class 1000 clean room area

- Comfort a/c (indoor as well as outdoor units) for specified areas as per layout

- Double skin wall paneling with GI sheet and PUF insulation for partitions in all other areas except class 1000 areas

- Epoxy wall painting and Epoxy ceiling painting for all other areas except class 1000 clean room area

- All covings inside clean room and outside the clean room

# SITE CONDITIONS

- Temperature			:		Maximum 38 Deg.C.

Minimum 18 Deg.C.

- Humidity				:		65%-95%

- Rainfall				:		Around 3000mm per annum.

- Altitude				:		Less than 500 meters from MSL.

2. ELECTRIC SUPPLY PARTICULARS

- Nominal voltage			:		415 Volts.

- Frequency			:		50 Hertz.

- Number of wires		:		3 phase and Neutral.

- Neutral earthing			:		Solidly earthed.

# 3. STANDARDS

The installation and components thereon shall conform to the requirements of   following specifications:-

i.	ISO 14644 2004/Schedule M:	Clean rooms & associated controlled

environments.

ii.	NBC 				:	National Building Code.

4. DRAWINGS

Following drawings will be the part of this tender:-

- General Layout Drawing

Drawing attached is only for reference purpose, the contractors are instructed to visit the site and submit their bid based on the actual site condition. Contractor shall prepare all working drawings including ducting and supporting steel work for the execution. And drawings if any required by statutory bodies and obtain necessary approvals. All such working drawings to be approved by the client / consultant.

  - BILL OF QUANTITIES

The quantities mentioned in the bill of quantities are for the guidance of the bidder to quote. The client/consultant do not in any way guarantee that the actual work will exactly correspond to the quantities now indicated. It shall be the contractor’s responsibility to procure only requisite quantity. The client reserves the right to add/delete any portion of the work within the project scope.

  - TESTING & VALIDATION

- Contractor shall do all necessary steps to integrate the proposed systems and components to the existing central system like chilled water line, plumbing line, FDA & building management system

- All equipments and materials included in contractor’s scope of design & supply shall be tested as per the relevant standards before delivery and necessary test certificates shall be submitted.

- All pre-commissioning tests shall be carried out after the installation is completed, and results shall be recorded.

- Contractor should carry out validation as per relevant standards, cGMP practices and Schedule-M guide lines and validation report along with as built drawings shall be submitted.

- Client will depute a third party inspection agency in addition to the validation covered in contractor’s scope of work for undertaking various relevant tests to ascertain clean room standards. If found defective during such inspection / Validation, contractor should carry out all corrective.

- Any rectification if found required may be carried out without any additional cost.

  - HANDING / TAKING OVER

The installation shall deem to have completed and taken over by the client         when:-

    - Entire installation is physically tested in the presence of client /

Consultant and results are satisfactory.

    - Obtaining final approval from statutory bodies including rectification of any defects pointed out during the third party inspection.

    - Contractor submits set of ‘AS BUILT’ drawings covering layouts and

Wiring diagram for the scope of work covered.

    - Contractor carries out all performance test & validation with satisfactory

results and submits all reports and completion certificates.

    - The defect liability period will start once contractor has completed all

formalities and commissioned the facility.

    - The installation and accessories shall be guaranteed for satisfactory

operation for a period 12 months from the date of handing over.  Any

defects noticed during this period shall be rectified free of cost.

  - INTERIOR PARTITIONS AND WORKS

# SCOPE

This part covers Requirements and Specifications for the clean room components associated with proposed class 1000 clean room facilities and associated comfort a/c rooms.

Contractor shall deploy a full time supervisor with sufficient experience in the

similar kind of project. The installation shall be carried out in accordance with good engineering practices available, latest Indian and International standards and specific requirements covered as below:-

CEILING PANELS

This shall be walkable type made with two skins of Pre painted Galvanized iron (PPGI) over an frame work sandwiched with PUF at the Micro biology Lab and Associated Change rooms and Corridors. Other areas there shall be no ceiling panels.  Other details shall be as per bill of quantities and drawing.

This shall be installed using proper supporting system installed from the existing RCC ceiling slab. Suitable cutouts shall be provided for installing luminaries and entering various service lines. Edges at cutout shall be duly finished.

WALL PANELS

This shall be made with two skins of PPGI over an frame work sandwiched with PUF. Other details shall be as per bill of quantities and drawing

Thickness of wall panels is as per drawings and bill of quantities. For 100mm wall panels return air duct made out of 20G aluminum shall be provided inside. This shall be connected to the main return air duct above ceiling.

Wall panels shall have a male edge one side and female edge on other side. This when two panels joined forms a sturdy interlock. Further the joints shall be finished with silicon sealant.

DOOR FRAME

Doors are fabricated from galvanized iron sheets duly powder coated. Maximum tolerance shall be 1 mm.

Thickness of the sheet shall be min 1.2 mm. The frame may be supplied in knock down form with joints. This shall be able to assemble at site easily using nut and bolts.

Hinge plates shall be recessed and manufactured with 5mm thick sheet and this shall be suitable for flush mounting for the hinges.

Reinforcement pads shall be used for fixing the automatic door closer.

SHUTTERS

Shutters are fabricated from galvanized iron sheets duly powder coated. Maximum tolerance shall be 1 mm.

This shall be 46 mm in thickness and made with 0.8 mm thick GI sheet. Core material shall be Fire retardant self extinguishing type EPS.

Hinges shall be 3mm thick and this shall be concealed type. All fasteners used shall be of machine screws.

Reinforcement pads shall be used for fixing the automatic door closer.

HVAC SYSTEM

- SCOPE

This part covers Requirements and Specifications for the clean room components associated with proposed class 1000 clean room facility for Micro Biology Lab area(Sterility).  The installation shall be carried out in accordance with good engineering practices (cGMP) available, latest Indian and International standards and specific requirements covered as below:-

- INSIDE CONDITIONS REQUIRED

- Air Flow type - Mixed

- Maximum Air Change/Hr - 80/Hr (For Class 1000 Clean Room ) .

- Fresh Air – 3ACPH

- Type of Filter - HEPA

- Overall Efficiency - 99.97% @ 0.3 micron.

- Location of HEPA Filter - At & Terminal filter

- Supply Air - From TOP.

- Return Air - Through Bottom side walls.

- Inside temperature - 22 +/- 2 Deg.C

- Relative Humidity – Not more than 60%

- AIR HANDLING UNITS

Indoor and Outdoor units shall be as specified in BoQ

- VARIABLE SPEED DRIVE

i . This shall be wall mounting type suitable for speed control of the AHU Fan.

- An alpha Numeric control panel with LCD display shall be provided which

can display and control minimum parameters as follows:- Local/Remote

Indication, Direction of rotation, Set speed, Actual Speed, Output current, Real

time clock.

- It shall be able to program various function parameters for different performance characteristics on a real time axis. There shall be suitable “swinging DC chokes” for reducing harmonics on available load conditions. Max THD shall not be more than 25%.

- Suitable RFI filters shall be provided.

- There shall be in built user friendly fault diagNotic feature.

- RS 485 port with built in modbus and sensor less vector control for better

motor performance.

- 2 No. built in PID controllers for any external device control like motorized           damper or valve.

- The equipment shall be supplied with necessary software & operating manual.

- DUCTING

- Aluminium sheets conforming to IS:737-1955.

- The ducting shall be tested for any kind of leakages.

- All ducting shall be applied with food grade RTV sealant on joints.

- All duct work shall be with Aluminum only and cross section shall be

rectangular.

- Duct routing should be straight with minimum deviations as far as possible.

- Minimum thickness of the ducting shall be 24 gauges.

- Sheet metal work shall be with good quality workman ship using right

engineering practices.

- Contractor shall prepare all working drawings and duct routing layout.

- Approval from the HLL shall be obtained before commencing the work.

- Extract panels with inbuilt ducts are envisaged for return air from the clean room.

- This extract panel will get connected to the return air duct network above

false ceiling and finally to the AHU.

- Acoustic lining shall be provided to the duct work near the AHU/TFA to

minimize the fan noise being transmitted through the duct work.

- It is essential to provide straightening vanes wherever there is a duct collar

joint for a proper balancing of air distribution.

- When there is change in duct size in a continuous run transformation duct

pieces have to be used. Normal slope shall be one in seven.

- Elbows shall have radius ratio 1.5 and maximum aspect ratio not more than six.

- Aspect ratio of rectangular duct should be within 4.

- In case of shorter elbows or sharp bends multiple turning vanes has to be used.

- Branch duct from a main duct (after an elbow) should be away at least 7.5

times of the elbow width.

- Ducts with thermal insulation shall be suspended from the roof slab using GI hi – tech support system with threaded rods and slotted strips.

- Cost of above supports shall be included in the item under duct in the BOQ.

- AIR FILTERS

- Multilevel air filtering is envisaged such as pre filter, fine filter and HEPA

filter for the class 1000 application.

- Pre filter will be required to filter out particle size upto 10 micron and fine filter will filter out 3 micron particles.

- Filters may be made out of micro layer fiber glass and asbestos and it should be fire and moisture resistant type. This should be of cleanable type.

- Normal pressure drop when pre filters are clean is around 6mm.

- The efficiency level shall be 99.9 % for 3 micron particles.

- All filters are located inside AHU / TFA unit and considered as a single entity.

- Rate quoted for AHU / TFA unit shall include necessary filters as specified.

- Terminal HEPA filters are to be located at the Microbiology Lab(Q-9), Corridor(Q-8), Change room-2, Gents & Ladies(Q-7) as per the attached drawings and should have an efficiency of 99.99% for 0.3 micron particles. Pressure drop may be around 50mm.

- Filters have to be fitted properly so that no leakage or by-pass may be present.

- Neoprene gaskets are used to seal the space between filter frame and

filter housing.

- Filters have to be installed only after cleaning the entire system properly.

- HEPA filter distribution is as follows

| Sl. No | Location | Dimension | Qty |
| --- | --- | --- | --- |
| 1 | Micro Biology Lab | 610X610X93 | 10 |
| 2 | Corridor | 300X300X93 | 2 |
| 3 | Changeroom-2 Gents | 300X300X93 | 1 |
| 4 | Change room-2 Ladies | 300X300X93 | 1 |
| 5 | Change room – 1 Gents | 300X300X93 | 1 |
| 6 | Change room-1 Ladies | 300X300X93 | 1 |

- Insulation

- Supply Air duct : 19mm thick chemically cross linked Closed cell polyethylene foam insulation material.

- Return Air duct : 13mm thick chemically cross linked Closed cell polyethylene foam insulation material.

- Terminal Filter boxes

Single skin insulated terminal filter housing made of SS304 shall be used for housing HEPA filter. This housing shall be provided with swirl diffuser.

- Return Air Risers

Return air risers are proposed to be constructed in integral with modular panels. Riser shall be provided with suitable return air grills and volume control damper.

- Filters Proposed

- Coarse Filter – 10 Micron – 60 - 80% efficiency (Synthetic Washable)

- Fine Filter-3 Micron – 99.9% efficiency (Synthetic Washable)

- Super Fine Filter – 1 Micron - 99.91% efficiency

- HEPA Filter – 0.3 Micron – 99.97 efficiency

(The above Filtration Level & efficiency is just for broad understanding, however all the filters have different range of efficiencies at different particle sizes and therefore for exact details refer to reputed filter manufacturer’s catalogue)

- Design Responsibility

The design of the entire HVAC System is the sole responsibility of the contractor. Therefore, Contractor is supposed to design the system and check the operating parameters, capacities of equipment etc. thoroughly before submitting the offer. The contractor will be responsible to demonstrate the system performance as per the intent. The preliminary design calculations have been carried out to facilitate the contractor to quote. However, if contractor feels that the capacity of the system indicated is not adequate, the contractor may submit the calculations for their appraisal.

ELECTRICAL SYSTEM

- SCOPE

This part covers Requirements and Specifications for the Electrical works associated with the proposed the New Micro biology Lab area. The installation shall be carried out in accordance with good engineering practices available, latest Indian and International standards and specific requirements covered as below:-

- SPECIFIC REQUIREMENTS

    - Electrical contractor shall have a valid license of appropriate class depending  upon  the size/capacity of the installation from the Kerala state Electricity licensing Board.

    - Electrical contractor shall deploy a full time supervisor with valid supervisory  license at site.

    - Contractor shall work in coordination with other agencies involved in the

project.

iv. All necessary documents including the drawings for approval from CEIG   & KSEB to be prepared by the contractor. No additional claim will be entertained for this part of the work.

- Any item if found necessary for the smooth completion of the job may be

included separately in the offer by the bidder.

vi.         Deviations if any shall be indicated clearly as a deviation statement.

- SWITCH BOARDS

- Location of the Switchboards shall be finalized and installed in consultation with the officials of HLL.

- Minimum clearance of 1.5 meters shall be maintained in front of the switchboard.

- Switchboards shall be aligned, leveled and grouted/bolted securely to

prevent any displacement.

- Earth bus of the switchboard shall be connected to the main earthing grid.

- Uncut gland plates supplied along the switchboard shall be properly cut for glanding the cables.

- Feeder designation shall be clearly painted / labeled on respective

feeders.

- Minimum operating height shall be 45Cms and Maximum shall be 180Cms.

- CABLES

- Cables shall be visually inspected before commencing the installation.

- Megger test has to be carried out for each feeder cable after glanding and

results shall be recorded.

- The LT power cable PVC insulated PVC sheathed shall be of the   Aluminum conductor and lower sizes shall be of copper conductor.

- Sharp bends and kinks shall be avoided in the installation. Bending radius

shall not be less than 12 times the diameter of the cable.

- Cable shall be laid one beside the other and not on top of each other. Adequate extra lengths shall be provided near all the terminations.

- Identification tags made out of Aluminum bearing cable number and size

shall be provided at either ends and at every 30mts of intervals.

- Cable glands shall be single compression SIBG type made out of extruded

brass and cadmium plated.

- End termination shall be of crimping type Al on the conductor type. Cable glands shall have earth tag and it shall be securely connected to the earthing system

- EARTHING

- The material for earthing shall be electrolytic grade bare copper.

- The end connection shall be of bolted type with suitable crimping type

terminal lugs.

- All equipment receiving three-phase connection shall have double earthing

and single-phase equipment shall have single earthing.

- All cable glands shall be earthed using earth tag/ copper clamps and

suitable size bare copper conductor.

- All non – current carrying metal parts shall be connected to the earthing                   system.

- Wherever joints or tap off are required, that area to be properly tinned.

- Lap joints in the conductors shall be with 50mm overlap.

- All hardware shall be GI.

- MCBs, RCCBs, & MCB DBs

- Factory assembled MCB DBs as per BOQ / SLD shall be wall mounting type.

- Suitable steel frame work if required shall be provided for installation                        where number of MCBDBs is more than one.

- Suitable fabricated wire ways shall be assembled between DBs on the

above framework for easy wiring and cable dressing.

- Body earthing (Double) to the main grid shall be strictly ensured.

- MCBs of proper rating as per SLD/wire size shall be arranged on the DIN

rail.

- All circuits shall be neatly terminated to the corresponding terminals and

proper dressing inside the DB shall be carried out.

- Circuit identification ferrules to be provided for each conductors of a circuit.

- Separate neutral and earth bus shall be provided and respective conductors of each circuit shall be connected to the above bus.

- Circuit identification, feeder identification and cable size shall be suitably

marked on the DB after the installation.

- ELCBs shall be of 30mA sensitivity and this shall be 4P or 2P as the case

may be. Usage of higher sensitivity ELCBs are not recommended.

- MCB rating based on wire/conductor size shall be as follows:-

-  1.0/1.5 Sq.mm – 6A

-  2.5 Sq. mm - 10A

-  4.0 Sq. mm - 16A

-  6.0 Sq. mm - 20A

- CONDUITS

- Unless otherwise specified all conduits for concealed and surface wiring

shall be of PVC black colour (M) duty.

- All accessories used shall be compatible each other.

- Maximum number of wires that can be drawn through a specified size of

conduit is as follows:-

| Size Cross of Conduit in mm | Sectional Area in Sq.mm |  |  |
| --- | --- | --- | --- |
|  | 20 | 25 | 32 |
| 1.5 | 5 | 10 | 14 |
| 2.5 | 5 | 8 | 12 |
| 4.0 | 3 | 8 | 10 |
| 6.0 | 2 | 5 | 8 |

- Conductors carrying different supply voltage shall be drawn through   separate    conduits.

- Only bends shall be used wherever conduits take right angle deviation and

no Elbows are permitted.

- All unused entries in the conduiting shall be blocked with thermo coal

packing so that cement mortar will not get into the conduiting during the

concreting.

- Fish wires shall be drawn through conduiting before concreting.

- Chipping using chisels shall be avoided to maximum extend.

- Conduits shall be properly clamped at every 60cms.

- For surface wiring, conduits shall be fixed by heavy gauge saddles to

suitable wood/pvc plug duly inserted in the wall etc, with GI screws

- WIRING

- Installation shall be divided into different circuits.

- Each circuits shall comprise of three conductors viz Phase, Neutral and earth.

- Phase and Neutral conductors shall be PVC insulated copper wire of size as specified.

- Earth conductor shall be generally of bare copper conductor/Green color PVC insulated wire of size as specified.

- Earth conductor size shall be of same size that of Phase conductor.

- Minimum size of wiring shall be 1.5 Sq.mm.

- MCB rating for each circuit shall be as per wire/conductor size and

specified else where.

- Generally circuits are classified as ‘Lighting’ ‘Power’ and ‘UPS’.

- Each circuit shall be connected to the respective DB (Lighting/Power/UPS)

- Maximum number of wires that can be drawn through a conduit is as

specified.

- Colour code shall be followed as far as possible and properly ferruled   with  yellow colour ferrules.

- Wiring from MCB DB to light switch boxes/socket location shall be termed as circuit wiring.

- Wiring from switchbox to light/fan point shall be termed as point wiring.

- Looping of Neutral and Earth conductor is permitted in point wiring.

- Number of points in each circuit is depends on the capacity/rating of the

circuit.

- LIGHT SWITCHES & BOXES

- This shall be generally of modular type. Metal boxes are preferred over PVC.

- Switchboxes shall be recess mounted in the wall.

- Required knock outs only shall be opened for conduit entry.

- Extra care shall be ensured while installation so that ‘plumb’ and ‘level’ shall be properly maintained.

- Front edge of the switchbox shall be in line with finished surface of the wall.

- Switch boxes shall be earthed using the earth conductor of respective circuit wiring.

- Height (from FFL) of Light switches shall be 125cms or as specified in the

drawings.

- Switchboxes shall be generally located 15cms from the edge of any door/

window or as per the aesthetic requirement as the case may be.

- Only one circuit shall be terminated in one switchbox. If more number of

circuits are required at one location separate switchboxes shall be

installed side by side.

- At least one blank space shall be provided in each switchbox.

- Switches shall be provided only on the phase conductor never on a neutral conductor.

- Telephone/Antenna/Data sockets shall be installed in separate switchboxes.

- Circuit identification with suitable permanent marking shall be provided on  each switch box.

- LUMINAIRES

- Type of luminaire shall be as specified in the bill of quantities. This shall be  complete with suitable type of lamps and control gear.

- All ballasts for the fluorescent lamps shall be Electronic (HF) type.

- Only Philips/Osram make high efficiency or equivalent fluorescent lamps

shall be used this shall be with.3250 lumens output for 4ft luminaires.

- Surface mounting Luminaires shall be directly installed to the ceiling / wall  using GI anchor fasteners

- Recess mounting luminaire shall be installed using suitable arrangements

like suspension chains from ceiling slab and weight of the luminaire shall

not be transferred to the false ceiling grid.

- For installation where false ceiling is employed, it is preferred to have a

common supporting system for conduits and luminaires.

- Threaded type of suspension system is preferred over steel bracket

- Earthing of the Luminaire body using respective earth conductor of point

wiring shall be ensured.

- Steel reinforced Flexible conduits with glands shall be used for wiring

(between ceiling junction box and luminaire) for recess mounting type.

- FIRE DETECTION AND ALARM SYSTEM

- DETECTORS

- Type :

: Photoelectric type.

: Rate of rise Heat Detectors.

- Manual Call Point

- Nominal Voltage	 : 24 V DC

- Sensitivity 		 : 0.67 to 3.77 obsc /ft.

- Temperature		 : 0 to 45 Deg. C

- Humidity			 : 0 to 90 % non condensing.

- Drift Compensation	 : Automatic about 1% / Ft.

- Diagnostics 		 : Self.

- Reset time 		 : 1Sec.

- Standby current         	 : 70 micro A. (aprox)

- LED Flash interval   	 : about 10 Sec.

- Alarm LED view      	 : 360 Degree

- Insects screen            	 : 0.508mm

- Temp. Rate of rise     	 : >105 Deg F & 15 Deg F / Min.

- Air Velocity               	 : Suitable for up to 1500 FPM.

- Shade                             : Off white.

- Protections                    : Against Transient surges.

: Polarity reversal.

: EMI & RF suppression.

- General Requirement    : Hermetically sealed solid state.

: Plug in type with Common base.

: Suitable for ceiling mounting.

: Field replaceable sensing chamber.

: Removable insect screen & Cover.

: Shield against dust & insect.

: Flashing LED while system healthy.

: Steady glowing LED at Alarm.

: Clean Me feature is desirable.

- INSTALLATION

- Conduiting shall be surface type and shall be 16G black enameled MS for

the FDA system. Minimum size shall be 20mm.

- Only threaded type of installation shall be carried out. Thread sealing

compound shall be used.

- No elbows are permitted but long radius bends.

- Fire red shade shall be applied for FDA conduiting.

- Wiring shall be of flame retardant low smoke type, 660volts grade, PVC

insulated shielded, flexible twin core with multistrand copper conductor.

- Cross sectional area shall be not less than 1.5 Sq.mm. – for FDA system.

- All passive components shall be interconnected using above conductor to

form a closed loop.

- Power supply for the hooter shall be through a separate network

originating from the control panel.

- Photoelectric type smoke detectors are proposed below false ceiling.

- Rate of rise type detectors are for the auto clave area.

- Response indicators shall be provided for the detectors above false

ceiling.

- This shall be located in the false ceiling to merge with reflected ceiling

layout.

- Type ‘A’ wiring to be adopted in which return wire through a separate

conduit shall be brought back to the FDA control panel.

- This return wiring shall be at least 30cms from loop conduiting.

- All testing as per relevant standard shall be carried out.

The detectors & MCPs shall be connected and synchronized  to the existing control panel already installed at the building.

#### APPROVED LIST OF VENDORS / SCHEDULE OF MAKES

| Sl No. | Items | Acceptable Makes |
| --- | --- | --- |
| 1 | Air Handling Units (Indoor & Outdoor) | Bluestar / Carrier / York |
| 2 | Magnehelic Gauges | DWYER / Waree. |
| 3 | Aluminium Sheets | Jindal/TATA/ SAIL. |
| 4 | Valves |  |
| a | Butterfly Valves | Audco/Honeywell/Advance/SKS |
| b | Non Return Valave | Advance/Honeywell/Danfoss |
| c | Balancing Valaves | Honeywell |
| d | Automatic Balancing Valve | Flowcon/ T A Hydronics/ Danfoss/ Honeywell |
| e | GM Gate Valve | GG/Leader |
| f | Ball Valve | BDK / AUDCO/GG/AUTOMATRIX |
| 5 | Insulation | Supreme/Trocellen |
| 6 | Air Washer | Zeco/Caryaire/Roots Cooling Systems |
| 7 | Motors | Siemens/Bharat Bijeee/Kirloskar/CG |
| 8 | Filters(Pre&Fine) | Thermadyne/Pyramid/Airtech/Chempharm/AAF |
| 9 | Filters(HEPA) | Chempharm/Thermadyne/Airtech/Pyramid/AAF |
| 10 | Duct Dampers | Caryaire/Ravistar/Airflow |
| 11 | Cables | RR/Finolex/LAP |
| 12 | Cable Gland | Denson/Comex/HEX |
| 13 | Lug | Dowells/Jaison/Multi |
| 14 | PVC Insulated copper wires | RR/Finolex/LAP/V Guard |
| 15 | Line Type Fuse | GE/Siemens/Havells |
| 16 | Terminal Block | Connectwell/Wago |
| 17 | Voltmeter/Ammeter/Energy Meter | Automatic Electric/Meco/Rishab/Conzerve |
| 18 | Indicating Lamps | Siemens/Teknik/Culter/Hammer/Jaibalaji |
| 19 | Selector Switches | Siemens/Kaycee |
| 20 | Switchgear | Siemens |
| 21 | MCB/MCBDB | Legrand/ABB/SCHNEIDER/SIEMENS |
| 22 | Modular Switches | Legrand |
| 23 | Industrial Plung & Socket | Legrand |
| 24 | Luminaire&Lamps | Philips/WIPRO/CG |
| 25 | FDA Control Panel | Honeywell/Hochiki |
| 26 | Detectors | Honeywell/Hochiki |
| 27 | Pump | IIT Bell&Gossett/Ground foss/Armstrong |
| 28 | Filter Cleaning Station | Air Tech/Pilani Envirotech/Whirlwing/ S A Air System |
| 29 | Return Air Motorised Dampers | Caryaire/Ravistar/Airflow |
| 30 | Fresh Air intake louvers | Caryaire/Ravistar/Airflow |
| 31 | Variable Frequency Drive | Allen Bradley |
| 32 | Conduit | BHARATH/VIP |
| 33 | Switches | Legrand |
| 34 | Air-conditioners Split | Bluestar / Voltas / Carrier |
| 35 | Voltage Stabilizers | V-Guard |

SECTION VI

GENERAL INFORMATIONS

(Please attach detailed pro-forma incorporating the information given below)

BID NO……………………….

DATE OF OPENING……..

NAME OF THE BIDDER:……………………………………..

1. Name & Full address of the Manufacturer

(a) PAN No                          (b). ECC Code                    (c) IEC if applicable

(d) CST No                          (e) TIN No                           (f)   Any other details

2. (a) Telephone No.: Office/Factory/Works

(b) Fax No.: Office/Factory/Works

(c) e-mail address:

- Location of the manufacturing factory

- Details of the process of manufacturer in the factory

- Details of staff proposed to be employed for this work

- Whether materials are tested to any standard specification?  If so, copies of

specifications & original test certificates should be submitted.

- Valid Electrical License No.(with validity period)

Signature and Seal of the Bidder ...................................

SECTION VII

PROFORMA FOR PERFORMANCE STATEMENT

DETAILS OF MAJOR INSTALLATIONS OF SIMILAR CLEAN ROOMS SUCCESSFULLY COMMISSIONED  BY THE TENDERER AS PRIME CONTRACTOR DURING THE LAST 3 YEARS

Bid No. HLL/AFT/PROJ/2016-17/07/MICROLAB/05

Name of the firm:

| Order placed by (Full Address of Purchaser) | Order No. And Date | Description | Value of order | Date of Completion | Remarks indicating reasons for delay, if any |
| --- | --- | --- | --- | --- | --- |

Signature and Seal of the Bidder ...................................

.

SECTION VII (a)

ANNEXURE – I

| DETAILS OF ONGOING SIMILAR INSTALLATIONS |  |  |  |
| --- | --- | --- | --- |
| Sl. No. | Name of Client with full address, telephone numbers and nature of work | ## Project details | Value of works (in lakhs) |

Signature and Seal of the Bidder ...................................

SECTION VII (a)

ANNEXURE – II

| FINANCIAL DETAILS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Financial Data | 12-13 | ## 13-14 | 14-15 | Average annual Turn Over turn over for last 3 years |
| Annual Turnover |  |  |  |  |

Gross Profit/Loss:

Whether attached the relevant Pages of Balance sheet and

Profit and Loss A/c duly certified By Chartered Accountant

Signature and Seal of the Bidder ...................................

SECTION VII (a)

ANNEXURE-III

DETAILS OF ORGANIZATION

| Sl.No | Name & Postal Address | Date of Birth | Qualification | Total experience in years | Name of organization served showing position held and period of service in each position |
| --- | --- | --- | --- | --- | --- |
| 1. 2 | # A.ENGINEERING PERSONNELS |  |  |  |  |
| 3. 4 |  |  |  |  |  |
| 5. 6 |  |  |  |  |  |
| 1. 2 | B.MANAGEMENT (NON TECHNICAL) |  |  |  |  |
| Attach an organization chart and resumes of all key technical persons for this project with their consent letters to work for this project. |  |  |  |  |  |

Signature and Seal of the Bidder ...................................

SECTION VII (a)

ANNEXURE IV

BIDDER'S EQUIPMENTS

LIST OF EQUIPMENTS

| SL.NO | EQUIPMENTS | NO.AVAILABLE | NO.PROPOSED TO BE DEPLOYED IN THIS PROJECT |
| --- | --- | --- | --- |

Signature and Seal of the Bidder ...................................

SECTION VII (a)

ANNEXURE V

CERTIFICATE

I / we hereby certify that the information given with this bidding document is correct. If, at any stage, it is found to be incorrect, I / we understand that the contract will be liable to be terminated and action could be taken against me/us by the Company for damages.

Signature and Seal of the Bidder ...................................

(To be submitted in the letter pad of the firm indicating full name and address, telephone & fax numbers etc.)

SECTION VII (b)

## HLL LIFECARE LIMITED

Akkulam Factory

THIRUVANANTHAPURAM-695017

HLL/AFT/PROJECTS/2016-17/07/MICROLAB/05

INDEMINITY CLAUSE

If the supplier fails to execute the order within the time prescribed for the Design, Fabrication, Supply, Erection, Validation and Commissioning of Micro Biology Laboratory ordered or violates or infringes the existing rates as agreed to as mentioned in the supply order, the supplier shall and will indemnify the company against all loses or damages whatsoever to be incurred or sustained including the legal cost or expenses incurred by the company by reason of non-delivery of Micro Biology Laboratory at agreed quantity and rate with in the time specified in the supply order.  The company will initiate legal action if the supplier fails to execute the supply order as per the schedule in the supply order for the actual loss suffered. No quantity tolerance will be permitted in this regard unless otherwise prior approval is taken by the company before dispatching any excess quantity supplied which shall be returned back on freight to pay basis at the risk of the supplier.   Responsiveness of the Bid shall be at the discretion of HLL.

The supplier shall have no right to change the quantity stipulated in the supply order.

Bid pronounced Non Responsive by HLL shall be summarily rejected.

The decision of HLL will be final and no correspondence of this shall be entertained.

We have read and understood the above conditions and agree to abide by the same.

PLACE:                                		NAME AND SIGNATURE OF THE APPLICANT

DATE:                                                         		 (WITH OFFICE SEAL)

SECTION VII (c)

## HLL LIFECARE LIMITED

Akkulam Factory

THIRUVANANTHAPURAM-695017

HLL/AFT/PROJECTS/2016-17/07/MICROLAB/05

#### DECLARATION

We confirm having read and understood all the specifications, instructions, forms, terms and conditions and other requirements of the above tender (both expressed and implied) in full and that we agree to abide by all without any deviation.

SEAL OF THE APPLICANT

SIGNATURE

NAME AND ADDRESS OF APPLICANT

SECTION - VIII

FORMAT FOR REQUISITION FOR SITE VISIT

TENDER NAME – Design, Fabrication, Supply, Erection, Validation & Commissioning of Micro Biology Lab at HLL LIFECARE LIMITED AKKULAM FACTORY, THIRUVANANTHAPURAM

IFB NO - HLL/AFT/PROJECTS/2016-17/07/MICROLAB/05

DATE OF TENDER –

DATE OF VISIT –

PURPOSE OF VISIT – SITE STUDY FOR PARTICIPATION IN TENDER

NAME OF ORGANIZATION –

ADDRESS FOR COMMUNICATION (REGISTERED OFFICE) -

PHONE:

FAX:

E-MAIL:

PARTICULARS   OF REPRESENTATIVES

| Sl No | Name | Designation |
| --- | --- | --- |
| 1. |  |  |
| 2. |  |  |

SECTION –IX

PRICE BID

SECTION IX

PRICE BID FORM

Date :..............................

IFB NO: HLL/AFT/PROJECTS/2016-17/07/MICROLAB/05

To:

HLL Lifecare Limited,

Akkulam Factory,

Sreekariam P.O.

Thiruvananthapuram – 17

Dear Sir

Having examined the Bidding Documents including Addenda No......................, the receipt of which is hereby duly acknowledged, we, the undersigned, offer to supply and deliver...........................................(Description of Goods and Services) in conformity with the said Bidding Documents for the sum of.............................. (Total Bid amount in Words and Figures) or such other sums as may be ascertained in accordance with the Schedule of Prices attached herewith and made part of this bid.

We agree to abide by price per unit mentioned in price schedule, for the bid validity period specified in the bid document and it shall remain binding upon us and may be accepted by you at any time before the expiration of that period.

Until a formal final contract is prepared and executed between us, this bid, together with your written acceptance of the bid and your notification of award, shall constitute a binding Contract between us. We understand that you are not bound to accept the lowest or any bid you may receive.

We confirm that we comply with the eligibility requirements as per ITB Clause 1 of the bidding documents.

Dated this ....... day of ............................ 20 ......

(signature)

(in the capacity of) __________________

Duly authorized to sign Bid for and on behalf of  _______________

HLL LIFECARE LIMITED

(A GOVERNMENT OF INDIA ENTERPRISE)

TENDER FOR DESIGN, FABRICATION, SUPPLY, ERECTION, VALIDATION AND COMMISSIONING OF MICRO BIOLOGY LABORATORY AT AKKULAM FACTORY, THIRUVANANTHAPURAM

PRICE ABSTRACT

| Sl No | Description | Supply (in Rs.) |  |  |  |  |  | Installation(in Rs.) |  |  |  | Grand Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Basic Amount | ED | CST / VAT (as applicable) | Freight, Insurance | WCT | Total | Basic Amount | Service Tax | WCT | Total |  |
| a | b | c | d | e | f | g | h = (c+e+f+g) | i | j | k | L = (i+j+k) | M = (h+L) |
| 1 | MODULAR PANEL AND CEILING |  |  |  |  |  |  |  |  |  |  |  |
| 2 | AIR CONDITIONING SYSTEM |  |  |  |  |  |  |  |  |  |  |  |
| 3 | ELECTRICAL ITEMS |  |  |  |  |  |  |  |  |  |  |  |
|  | GRAND TOTAL |  |  |  |  |  |  |  |  |  |  |  |

Price quoted should be based on the Make/Brand specified in the tender document. The bidders have to mention the Make/Brand proposed to use for the project.

The proof of remittance of PF & ESI charges to be submitted to HLL, otherwise statutory levies such as ESI, PF etc will be deducted from contractors bill as per rules.

Bidders shall have registration under Kerala VAT and shall produce necessary certificate from Kerala VAT authority for deduction at specified rate/non deduction of WCT, if any applicable under Kerala VAT.

In case the bidder do not have Kerala VAT registration WCT @ 10% as per Kerala VAT rules will be deducted from total contract value

Bidder shall supply the materials  with applicable CST /VAT etc and no “C” Form shall be issued by HLL against supplies.

Bidder shall provide Excise Invoice (manufacturer invoice / dealer invoice) for excisable goods under supply schedule

Seal and signature of the bidder

SECTION –IX (A)

PRICE SCHEDULE FOR SUPPLY

BILL OF QUANTITIES –

SUPPLY OF MODULAR WALLS, CEILING PANELS AND EPOXY WORKS

| SL NO | Description | Unit of Measurement (UOM) | Qty | Supply |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Base Rate |  |  | Basic Amount |  | ED (specify applicable ED) | Taxes (specify applicable taxes such as CST/VAT.etc.) | Freight, Insurance / other(s) if any. (specify) | Work Contract Tax | Amount |
| a | b | c | d | e |  |  | F= (d*e) |  | g | h | i | j | K = (f+g+h+i+J) |
| 1 | SUPPLY OF MODULAR PARTITIONS |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Self supporting wall provided in modular units consisting of external skin in Pre painted Galvanized Iron (PPGI) which will be 0.6mm thick, with protective film to prevent surface damage during shipping and installation. |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 | Panel Thickness: 50mm | Sqm | 210 |  |  |  |  |  |  |  |  |  |  |
| 1.2 | Panel Thickness: 100mm | Sqm | 90 |  |  |  |  |  |  |  |  |  |  |
|  | Movable wall includes: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) PUF insulation 40 Kg/m3 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) GI frame work. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) Silicon sealant (Clear, White, Winsil Gray) |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | SUPPLY OF FALSE CEILING | Sqm | 35 |  |  |  |  |  |  |  |  |  |  |
| 2.1 | False ceiling panels are designed to fit within each other and suspended by threaded tension bars with adjustable turnbuckles fastened to the overhead support at fixed intervals, Standard Ceiling Panels are 50 mm thick and have a composite construction of two skins of PPGI over an frame work with a sealed and insulated interior. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Type :- Walkable |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Panel Thickness: 50mm (PPGI ) |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Ceiling includes |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a) PUF insulation 40 Kg/m3 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b) Sheet Thickness 0.6mm |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c) GI frame work. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | d) Special load bearing Aluminum connecting profile between ceiling panels at provide the precision 3-4 mm seal gap to bottom and inbuilt hanging arrangement at top. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | e) Silicon sealant (Clear, White, Winsil Gray) |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | SUPPLY OF COVINGS AND WALL CONNECTIONS |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.1 | Extruded Aluminum Powder Coated /Anodized R60 clip on type covings for Wall to Wall double skin Panels. | Rmt | 355 |  |  |  |  |  |  |  |  |  |  |
| 3.2 | Aluminum Powder Coated / Anodized 3 D internal Corner Piece | No | 80 |  |  |  |  |  |  |  |  |  |  |
| 3.3 | Standard Epoxy floor covings of R50 | Rmt | 75 |  |  |  |  |  |  |  |  |  |  |
| 3.4 | Standard Gypsum covings of R50 between roof ceiling and wall panels | Rmt | 50 |  |  |  |  |  |  |  |  |  |  |
| 4 | SUPPLY OF CLEAN ROOM DOORS |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Doors are designed to fit flush into the wall panel system on both sides and are supplied in different dimensions. Doors are fabricated from galvanised iron sheets duly powder coated. Shutter has sheet thickness of 0.8mm and the frame of 1.2mm. Standard 50 mm panel has frame width of 50 mm and shutter width of 46mm. Doors are available in various sizes as per the requirement of the client. The following accessories are a part of the door: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Shutter Thickness: 46 mm thick |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Stainless steel hinges |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Stainless Steel 'D' type of handles on pull side |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Stainless steel push plates on push side. |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Dorma/geze make standard arm door closure (TS-68) |  |  |  |  |  |  |  |  |  |  |  |  |
|  | View panel along with self adhesive tape and silicon sealant |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Filler material : Puff |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Door clear Opening Size |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.1 | Single Door (Size: 1000x 2100 ) D2 | No | 4 |  |  |  |  |  |  |  |  |  |  |
| 4.2 | Single Door (Size: 750 x 2100 ) D1 | No | 15 |  |  |  |  |  |  |  |  |  |  |
| 4.3 | 6mm thick View glass set (Size: 1000 x 1000 ) | No | 3 |  |  |  |  |  |  |  |  |  |  |
| 5 | Supply of Riser | No | 10 |  |  |  |  |  |  |  |  |  |  |
| 6 | Supply of Ceiling Cutout | No | 34 |  |  |  |  |  |  |  |  |  |  |
| 7 | Supply of Emergency Exit breakable glass / Emergency escape Door | No | 2 |  |  |  |  |  |  |  |  |  |  |
| 8 | Supply of Pass Box |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.1 | Dynamic pass box 1/4 HP Blower motor 2 No. of Prefilter 5 Micron 1 No. of Hepa filter miniplate 0.399micron 0 to 25wg Magnehelic guage for pressure indicator C TYPE HANDLE PROVIDED Perforated sheet provide for return air Both side provide door in design inside double door toughened double body with viewing window double body type glass in made out from SS 304 18 swg prime sheet window Finish in Matt Polish Air Pressure must be 60 ACH Dynamic Two door Pass Box 600(L)x600(W)x 600(D) mm | No | 1 |  |  |  |  |  |  |  |  |  |  |
| 8.2 | Dynamic Three door pass box 600(L)x600(W)x 600(D) mm | No | 1 |  |  |  |  |  |  |  |  |  |  |
| 8.3 | Static pass box 600(L)x600(W)x 600(D) mm | No | 2 |  |  |  |  |  |  |  |  |  |  |
| 9 | Supply of GI sheet & necessary frame structure for Closing under side beam level gap with powder coated | Sq.m | 10 |  |  |  |  |  |  |  |  |  |  |
| 10 | Epoxy Flooring | Sq.m | 175 |  |  |  |  |  |  |  |  |  |  |
|  | Providing epoxy self leveling flooring systems of average 3mm thickness, with priming, with self levelling epoxy manufactured by M/s BASF/MRF/SIKA/ERDEX/Cipy/Grand polycoat Construction Chemicals India Pvt. Ltd, or equivalent approved, over cementitious substrate, after cleaning the surface free from all loose particles, laitance, patching of small patches, nicks etc, with Epoxy putty, applying Epoxy primer, in the coverage rate recommended by manufacturer, and thereafter spreading 4 component self leveling epoxy compound, at a coverage rate recommended by manufacturer, tooling and finishing to gloss/matt finish, as directed by engineer in charge, including all materials and labor with two years warrantee against materials and application defects. |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 | Epoxy wall painting | Sq.m | 80 |  |  |  |  |  |  |  |  |  |  |
|  | Providing epoxy coating to walls and beams, to an average thickness of 500 microns, with MASTERTOP 1120 t manufactured by M/s BASF Construction Chemicals India Pvt. Ltd, or equivalent approved, after applying cement based putty to the parent sound surface, finishing and thereafter applying one primer coat and two body coats of Mastertop 1120 T, after demolshing the existing wall paint in the enter surface of damaged area, including all materials, labour etc, with 2 years quarantee against materials and application defects. |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 | Epoxy painting of ceiling | Sq.m | 250 |  |  |  |  |  |  |  |  |  |  |
|  | Providing epoxy coating to ceiling, to an average thickness of 500 microns, with MASTERTOP 1120 t manufactured by M/s BASF Construction Chemicals India Pvt. Ltd, or equivalent approved, after applying cement based putty to the parent sound surface, finishing and thereafter applying one primer coat and two body coats of Mastertop 1120 T, after demolshing the existing wall paint in the enter surface of damaged area, including all materials, labour etc, with 2 years quarantee against materials and application defects. |  |  |  |  |  |  |  |  |  |  |  |  |
| GRAND TOTAL |  |  |  |  |  |  |  |  |  |  |  |  |  |

*Actual quantity is taken against installation and measurement

Seal and Signature of the bidder

BILL OF QUANTITIES – SUPPLY OF HVAC SYSTEM

| SL NO | Description | Unit of Measurement (UOM) | Qty | Supply |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Base Rate | Basic Amount |  | ED (specify applicable ED) | Taxes (specify applicable taxes such as CST/VAT.etc.) | Freight, Insurance / other(s) if any. (specify) | Work Contract Tax | Amount |
| a | b | c | d | e | F= (d*e) |  | g | h | i | j | K = (f+g+h+i+J) |
| 1 | Supply of 5.5 TR Capacity Air cooled scroll condensing Outdoor unit Condensing unit with hermetic scroll compressors and eco friendly R 407 C refrigerant. |  |  |  |  |  |  |  |  |  |  |
| 1.1 | Capacity - 5.5 TR Scroll Outdoor Condensing Unit | No | 1 |  |  |  |  |  |  |  |  |
| 2 | Supply of Floor mounted DIDW Air Air Handling Unit with 40mm thick Thermal Break Profile with powder coated outer of double skin of 0.6 mm thick and 0.6 mm inner thick. The AHU coil shall be DX type cooling coil and energy efficient motor..The Air Handling Units with combination pre filter ,Fine filter,super fine filter and hepa filter in the unit. |  |  |  |  |  |  |  |  |  |  |
| 2.1 | Capacity : 4000 cfm with 130 mm TSP (5.5 TR), 6RD | No | 1 |  |  |  |  |  |  |  |  |
| 3 | Copper Piping With Accessories |  |  |  |  |  |  |  |  |  |  |
| 3.1 | Supply of Hard drawn Copper pipe as per below mentioned sizes. The suction & liquid line shall be insulated with 9 mm thick Sleeveless nitrile rubber insulation and the approximate distance between the Indoor unit & Outdoor unit horizontal length shall be 10 mtrs and vertical length shall be approximately 4 mtrs below Indoor unit. The cost power cabling between indoor to outdoor unit & Control panel also have to be included in this section. |  |  |  |  |  |  |  |  |  |  |
| a | 1 3/8" dia Suction line & 7/8" dia liquid line pipe | Rmt | 20 |  |  |  |  |  |  |  |  |
| b | Drier Core | Nos. | 1 |  |  |  |  |  |  |  |  |
| c | Refrigerant R407C First Charge | Kgs | 7 |  |  |  |  |  |  |  |  |
| d | Shut Off Valve Set | Nos. | 1 |  |  |  |  |  |  |  |  |
| e | Liquid Line Moisture Indicator | Nos. | 1 |  |  |  |  |  |  |  |  |
| f | Expansion Valve | Nos. | 1 |  |  |  |  |  |  |  |  |
| 4 | SUPPLY OF AIR DISTRIBUTION SYSTEM |  |  |  |  |  |  |  |  |  |  |
|  | Supply of Aluminum Ducting material |  |  |  |  |  |  |  |  |  |  |
|  | Aluminum ducting with all accessories like Bends, Tees, Reducer, expander, Turning vanes etc. with RTV sealant |  |  |  |  |  |  |  |  |  |  |
| 4.1 | 20 G | Sqm | 80 |  |  |  |  |  |  |  |  |
| 4.2 | 22 G | Sqm | 80 |  |  |  |  |  |  |  |  |
| 5 | SUPPLY OF THERMAL INSULATION MATERIAL |  |  |  |  |  |  |  |  |  |  |
| 5.1 | Supply of Al.Foil faced Thermal insulation on ducts of 13mm thick closed cell nitrile rubber | Sqm | 100 |  |  |  |  |  |  |  |  |
| 5.2 | Supply of acoustic insulation for supply air ducts with 10mm thick open cell nitrile rubber. | Sqm | 100 |  |  |  |  |  |  |  |  |
| 6 | SUPPLY OF TERMINAL BOXES WITH FILTER |  |  |  |  |  |  |  |  |  |  |
|  | Filter box in 20 swg GI CRCA powder coated suitable for following with gear operated VCD for supply air with 0.3 Micron HEPA filters with Aluminium powder coated perforated sheet |  |  |  |  |  |  |  |  |  |  |
| 6.1 | 610 x 610 x 93 | No | 10 |  |  |  |  |  |  |  |  |
| 6.2 | 300 x 300 x 93 | No | 6 |  |  |  |  |  |  |  |  |
| 7 | SUPPLY OF RETURN AIR RISERS GRILL WITH FILTER |  |  |  |  |  |  |  |  |  |  |
| 7.1 | Powder coated riser complete with aluminum powder coated perforated sheet & 20 micron filter for return air riser with volume control dampers. | Sqm | 15 |  |  |  |  |  |  |  |  |
| 8 | SUPPLY OF Diffuser / Grill / Damper |  |  |  |  |  |  |  |  |  |  |
| 8.1 | Supply air Diffusers in extruded aluminum construction with Volume control Damper. | Sqm | 3 |  |  |  |  |  |  |  |  |
| 8.2 | Supply air Diffusers in extruded aluminum construction without Volume control Damper | Sqm | 3 |  |  |  |  |  |  |  |  |
| 8.3 | Extruded Aluminium Volume control dampers Low leakage type aero foil blade sections 100mm wide opposite blade operation ,blade linkage with operating gear fully enclosed and stainless steel side seal gaskets. | Sqm | 1 |  |  |  |  |  |  |  |  |
| 9 | SUPPLY OF FIRE / SMOKE DAMPER |  |  |  |  |  |  |  |  |  |  |
| 9.1 | Supply of GI 16g construction Fire Dampers with extended shaft for actuator mounting. The fire damper are rated for 90 minutes with fusible link designed to melt at 70°C. | Sqm | 1 |  |  |  |  |  |  |  |  |
| 9.2 | Supply of fusible link for above fire dampers. | No | 2 |  |  |  |  |  |  |  |  |
| 10 | Supply of condensate Drain piping 10 RMT per Air Handling unit |  |  |  |  |  |  |  |  |  |  |
| 10.1 | Drain piping using water quality blue HDPE pipe with GI fittings 32mm with 6mm thick nitrile rubber insulation | mtr | 20 |  |  |  |  |  |  |  |  |
| 11 | Remote push button stations |  |  |  |  |  |  |  |  |  |  |
| 11.1 | Remote push button stations consisting of one no. ON and one no.OFF illumiinated type push buttons housed in a MS box and having SS top cover plate | No. | 2 |  |  |  |  |  |  |  |  |
| 12 | Thermostat | No | 2 |  |  |  |  |  |  |  |  |
| E | MISCELLANEOUS ITEMS |  |  |  |  |  |  |  |  |  |  |
| 13 | Magnahelic Guage in core areas with MS powder coated box with SS 304 Flush cover | No | 6 |  |  |  |  |  |  |  |  |
| 14 | Magnahelic Guage for AHU across each filter | No | 4 |  |  |  |  |  |  |  |  |
| 15 | M.S Angle work for support if required | KG | 500 |  |  |  |  |  |  |  |  |
|  | GRAND TOTAL |  |  |  |  |  |  |  |  |  |  |

*Actual quantity is taken against installation and measurement

Seal and Signature of the bidder

BILL OF QUANTITIES – SUPPLY OF ELECTRICAL ITEMS

| SL NO | Item | Unit of Measurement (UOM) | Qty | Supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Base Rate |  |  |  |  | Basic Amount |  | ED (specify applicable ED) | Taxes (specify applicable taxes such as CST/VAT.etc.) |  | Freight, Insurance / other(s) if any. (specify) |  | Work Contract Tax |  |  | Amount |
| a | b | c | d | e |  |  |  |  | F= (d*e) |  | g | h |  | i |  | j |  |  | K = (f+g+h+i+J) |
| 1 | Supply of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 8 way (4 + 36), Double door (Main DB) | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | Supply of Cable End Termination Box of sheet steel, dust protected, duly powder painted, suitable for surface mounting, vertical type, 8 Way TPN MCB | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Supply of following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 4 way (4 + 12), Single door (LDB) | No | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | Supply of Cable End Termination Box of sheet steel, dust protected, duly powder painted, suitable for surface mounting, vertical type, 4 Way TPN MCB | No | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | Supply of following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 63 amps (Main DB) | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 | Supply of following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 40 amps (LDB) | No | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 | Supply of Single Pole (SP) MCB "C" Curve in the existing MCB DB complete with connections as required |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 6 amps | No | 16.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 20 amps | No | 16.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | 32 amps | No | 4.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 | Supply of Triple Pole (TP) MCB "C" Curve in the existing MCB DB complete with connections as required |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 20 amps | No | 4.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 32 amps | No | 5.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | 40 amps | No | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 | Supply of single pole blanking plate in the existing MCB DB complete etc. as required. | No | 20.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 | Wire for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required. (Two light points are controlled by ONE Switch & ONE 5/6 Amps Socket with ONE SWITCH) | No | 40.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 | Supply of following size/ modules, GI / PVC box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 2 Module | No | 8.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 3 Module | No | 16.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | 4 Module | No | 12.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| d | 6 Module | No | 15.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e | 8 Module | No | 6.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 | Supply of following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 5/6 amps switch | No | 40.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 15/16 amp switch | No | 5.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | 3 pin 5/6 amp socket outlet | No | 15.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| d | 6 pin 15/16 amp socket outlet | No | 5.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e | RJ 11 Telephone socket outlet | No | 4.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f | RJ 45 CAT 6 Data Socket Outlet | No | 4.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 | Supply of Single Door PVC Telephone Krone Junction Box for the termination of 10 Pair Telephone Cable with 10 pair Connection Module etc. as required. | No | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 | Supply of 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let as required. | No | 10.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | Supply of 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out as required. | No | 4.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 | Wire for circuit/submain wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in existing surface/recessed medium class PVC conduit as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 2X1.5 sq.mm + 1X1.5 sq.mm earth wire | mtr | 500.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | mtr | 250.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | mtr | 250.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 | Supplying of following pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 2 Pair | mtr | 300.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 10 Pair | mtr | 50.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 | Supply of CAT 6 UTP Cable in the existing surface/ recessed steel/ PVC conduit as required. | mtr | 100.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 | Supply of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 20 mm | mtr | 250.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 25 mm | mtr | 300.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | 32 mm | mtr | 200.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 | Supply of one number PVC insulated and PVC sheathed / XLPE Armoured power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 2 X 1.5 sq. mm | mtr | 50.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 3 X 4 sq. mm | mtr | 30.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | 4 X 6 sq.mm | mtr | 30.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| d | 4 X 10 sq. mm (22mm) | mtr | 20.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e | 4 X 16 sq. mm (25mm) | mtr | 50.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f | 3 1/2 X 35 sq. mm (28mm) | mtr | 100.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 21 | Supply of end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 2 X 1.5 sq. mm | No | 6.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 3 X 4 sq. mm | No | 4.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | 4 X 6 sq.mm | No | 4.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| d | 4 X 10 sq. mm | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e | 4 X 16 sq. mm | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f | 3 1/2 X 35 sq. mm | No | 4.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22 | Termination of one number PVC insulated Unarmoured 0.5 sq mm annealed copper conductor 10 Pair cable | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 23 | Termination of CAT 6 UTP Cable | No | 8.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 24 | Supply of Copper Wire for Earthing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | 6 SWG | Rmtr | 250.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | 10 SWG | Rmtr | 200.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 | Supply of pre wired Box type Light Fixture with 4 Feet 2 X 18/20 W LED Tube Light provided with opal polysterene diffuser as required | No | 12.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 | Supply of pre wired Clean Room Light Fixture with 2 X 2 Feet LED Light fitting, 55 +/- 10 W (Recess Mounting) provided with opal polysterene diffuser as required | No | 18.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 27 | Supply of pre wired Recessed mounted, Circular Down Light, LED 5 /8 W as required | No | 8.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 28 | Supply of pre wired Exhaust Fan, Industrial Type, 18", Single Phase, | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 29 | Supply of Aluminium/PVC Louvers for Industrial Type, 18" Exhaust Fan, | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 | Supply of pre wired Variable Frequency Drive suitable for 3 HP AHU Blower in powder coated sheet steel enclosure with ON & OFF Push Buttons, Indication Lamps for ON & OFF, Ventilation Fan and Air Inlet Louver, etc. | No | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | Supply of pre wired 1.5 Ton Split AC Unit having 5 Star Rating with suitable Stabilizer, etc. complete. | No | 3.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 32 | Supply of Split AC Unit of capacity 3.00 TR and having 5 Star Rating with suitable Stabilizer, etc. | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 33 | Fire Detectors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a | Photo electric type smoke detectors. | No | 16.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b | Rate of rise type detectors for autoclave area. | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c | Fault Isolation module. | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| d | Response Indicators. | No | 18.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e | Manual call points with break glass. | No | 2.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 34 | Supply of AHU Star / Delta starter Panel with cabling from starter panel to AHU Motor. The cabling considered shall be 10 rmt. | No | 1.00 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

*Actual quantity is taken against installation and measurement

Seal and Signature of the bidder

bidder

SECTION IX (B)

PRICE SCHEDULE FOR INSTALLATION

BILL OF QUANTITIES – INSTALLATION OF MODULAR PARTITIONS, CEILING AND EPOXY WORKS

| SL NO | Item | Unit of Measurement (UOM) | Qty | INSTALLATION |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Base Rate | Basic Amount | Service tax (specify applicable Service Tax) | Work Contract Tax (specify applicable WCT) | Amount |
| a | b | c | d | e | F= (d*e) | g | h | I= (f+g+h) |
| 1 | Self supporting wall provided in modular units consisting of external skin in Pre painted Galvanized Iron (PPGI) which will be 0.6mm thick ,with protective film to prevent surface damage during shipping and installation. |  |  |  |  |  |  |  |
| 1.1 | Panel Thickness: 50mm | Sqm | 210 |  |  |  |  |  |
| 1.2 | Panel Thickness: 100mm | Sqm | 90 |  |  |  |  |  |
|  | Movable wall includes: |  |  |  |  |  |  |  |
|  | a) PUF insulation 40 Kg/m3 |  |  |  |  |  |  |  |
|  | b) GI frame work. |  |  |  |  |  |  |  |
|  | c) Silicon sealant (Clear, White, Winsil Gray) |  |  |  |  |  |  |  |
| 2 | FALSE CEILING |  |  |  |  |  |  |  |
| 2.1 | False ceiling panels are designed to fit within each other and suspended by threaded tension bars with adjustable turnbuckles fastened to the overhead support at fixed intervals , Standard Ceiling Panels are 50 mm thick and have a composite construction of two skins of PPGI over an frame work with a sealed and insulated interior. |  |  |  |  |  |  |  |
|  | Type :- Walkable |  |  |  |  |  |  |  |
|  | Panel Thickness: 50mm (PPGI ) | Sqm | 35 |  |  |  |  |  |
|  | Ceiling includes |  |  |  |  |  |  |  |
|  | a) PUF insulation 40 Kg/m3 |  |  |  |  |  |  |  |
|  | b) Sheet Thickness 0.6mm |  |  |  |  |  |  |  |
|  | c) GI frame work. |  |  |  |  |  |  |  |
|  | d) Special load bearing Aluminium connecting profile between ceiling panels at provide the precision 3-4 mm seal gap to bottom and inbuilt hanging arrangement at top. |  |  |  |  |  |  |  |
|  | e) Silicon sealant(Clear,White, Winsil Gray) |  |  |  |  |  |  |  |
| 3 | COVINGS AND WALL CONNECTIONS |  |  |  |  |  |  |  |
| 3.1 | Extruded Aluminium Powder Coated /Anodised R60 clip on type covings for Wall to Wall double skin Panels. | Rmt | 355 |  |  |  |  |  |
| 3.2 | Aluminium Powder Coated / Anodised 3 D internal Corner Piece | No | 80 |  |  |  |  |  |
| 3.3 | Standard Epoxy floor covings of R50 | Rmt | 75 |  |  |  |  |  |
| 3.4 | Standard Gypsum covings of R50 between roof ceiling and wall panels | Rmt | 50 |  |  |  |  |  |
| 4 | CLEAN ROOM DOORS |  |  |  |  |  |  |  |
|  | Doors are designed to fit flush into the wall panel system on both sides and are supplied in different dimensions. Doors are fabricated from galvanised iron sheets duly powder coated. Shutter has sheet thickness of 0.8mm and the frame of 1.2mm. Standard 50 mm panel has frame width of 50 mm and shutter width of 46mm. Doors are available in various sizes as per the requirement of the client. The following accessories are a part of the door: |  |  |  |  |  |  |  |
|  | Shutter Thickness: 46 mm thick |  |  |  |  |  |  |  |
|  | Stainless steel hinges |  |  |  |  |  |  |  |
|  | Stainless Steel 'D' type of handles on pull side |  |  |  |  |  |  |  |
|  | Stainless steel push plates on push side. |  |  |  |  |  |  |  |
|  | Dorma/geze make standard arm door closure (TS-68) |  |  |  |  |  |  |  |
|  | View panel along with self adhesive tape and silicon sealant |  |  |  |  |  |  |  |
|  | Filler material : Puff |  |  |  |  |  |  |  |
|  | Door clear Opening Size |  |  |  |  |  |  |  |
| 4.1 | Single Door (Size: 1000x 2100 ) D2 | No | 4 |  |  |  |  |  |
| 4.2 | Single Door (Size: 750 x 2100 ) D1 | No | 15 |  |  |  |  |  |
| 4.3 | 6mm thick View glass set (Size: 1000 x 1000 ) | No | 3 |  |  |  |  |  |
| 5 | Riser | No | 10 |  |  |  |  |  |
| 6 | Ceiling Cutout | No | 34 |  |  |  |  |  |
| 7 | Emergency Exit breakable glass | No | 2 |  |  |  |  |  |
| 8 | Pass Box |  |  |  |  |  |  |  |
| 8.1 | Dynamic pass box 1/4 HP Blower motor 2 No. of Prefilter 5 Micron 1 No. of Hepa filter miniplate 0.399micron 0 to 25wg Magnehelic guage for pressure indicator C TYPE HANDLE PROVIDED Perforated sheet provide for return air Both side provide door in design inside double door toughened double body with viewing window double body type glass in made out from SS 304 18 swg prime sheet window Finish in Matt Polish Air Pressure must be 60 ACH 600(L)x600(W)x 600(D) mm | No | 1 |  |  |  |  |  |
| 8.2 | Dynamic Three door pass box 600(L)x600(W)x 600(D) mm | No | 1 |  |  |  |  |  |
| 8.3 | Static pass box 600(L)x600(W)x 600(D) mm | No | 2 |  |  |  |  |  |
| 9 | Using GI sheet & necessary frame structure for Closing under side beam level gap with powder coated | Sq.m | 10 |  |  |  |  |  |
| 10 | Epoxy Flooring | Sq.m | 175 |  |  |  |  |  |
|  | Applying epoxy self leveling flooring systems of average 3mm thickness, with priming coat in proposed PEB at terrace floor , with self levelling epoxy manufactured by M/s BASF/MRF/SIKA/ERDEX/Cipy/Grand polycoat Construction Chemicals India Pvt. Ltd, or equivalent approved, over cementitious substrate, after cleaning the surface free from all loose particles, laitance, patching of small patches, nicks etc, with Epoxy putty, applying Epoxy primer, in the coverage rate recommended by manufacturer, and thereafter spreading 4 component self leveling epoxy compound, at a coverage rate recommended by manufacturer, tooling and finishing to gloss/matt finish, as directed by engineer in charge, including all materials and labor with two years warrantee against materials and application defects. |  |  |  |  |  |  |  |
| 11 | Epoxy wall painting | Sq.m | 80 |  |  |  |  |  |
|  | Applying epoxy coating to walls and beams, to an average thickness of 500 microns, with MASTERTOP 1120 t manufactured by M/s BASF Construction Chemicals India Pvt. Ltd, or equivalent approved, after applying cement based putty to the parent sound surface, finishing and thereafter applying one primer coat and two body coats of Mastertop 1120 T, after demolshing the existing wall paint in the enter surface of damaged area, including all materials, labour etc, with 2 years quarantee against materials and application defects. |  |  |  |  |  |  |  |
| 12 | Epoxy painting of ceiling | Sq.m | 250 |  |  |  |  |  |
|  | Applying epoxy coating to ceiling, to an average thickness of 500 microns, with MASTERTOP 1120 t manufactured by M/s BASF Construction Chemicals India Pvt. Ltd, or equivalent approved, after applying cement based putty to the parent sound surface, finishing and thereafter applying one primer coat and two body coats of Mastertop 1120 T, after demolshing the existing wall paint in the enter surface of damaged area, including all materials, labour etc, with 2 years quarantee against materials and application defects. |  |  |  |  |  |  |  |
|  | GRAND TOTAL |  |  |  |  |  |  |  |

*Actual quantity is taken against installation and measurement

SEAL AND SIGNATURE OF THE BIDDER :

BILL OF QUANTITIES - INSTALLATION  OF HVAC SYSTEM

| SL NO | Item | Unit of Measurement (UOM) | Qty | INSTALLATION |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Base Rate | Basic Amount | Service tax (specify applicable Service Tax) | Work Contract Tax (specify applicable WCT) | Amount |
| a | b | c | d | e | F= (d*e) | g | h | I= (f+g+h) |
| 1 | Supply of 5.5 TR Capacity Air cooled scroll condensing Outdoor unit Condensing unit with hermetic scroll compressors and eco friendly R 407 C refrigerant. |  |  |  |  |  |  |  |
| 1.1 | Capacity - 5.5 TR Scroll Outdoor Condensing Unit | No | 1 |  |  |  |  |  |
| 2 | Supply of Floor mounted DIDW Air Handling Unit with 40mm thick Thermal Break Profile with powder coated outer of double skin of 0.6 mm thick and 0.6 mm inner thick. The AHU coil shall be DX type cooling coil and energy efficient motor. The Air Handling Units with combination pre filter ,Fine filter and hepa filter in the unit. |  |  |  |  |  |  |  |
| 2.1 | Capacity : 2000 cfm with 100 mm TSP (5.5 TR), 6RD | No | 1 |  |  |  |  |  |
| 3 | Copper Piping With Accessories |  |  |  |  |  |  |  |
| 3.1 | Supply of Hard drawn Copper pipe as per below mentioned sizes. The suction & liquid line shall be insulated with 9 mm thick Sleeveless nitrile rubber insulation and the approximate distance between the Indoor unit & Outdoor unit horizontal length shall be 10 mtrs and vertical length shall be approximately 4 mtrs below Indoor unit. The cost power cabling between indoor to outdoor unit & Control panel also have to be included in this section. |  |  |  |  |  |  |  |
| a | 1 3/8" dia Suction line & 7/8" dia liquid line pipe | Rmt | 20 |  |  |  |  |  |
| b | Drier Core | Nos. | 1 |  |  |  |  |  |
| c | Refrigerant R407C First Charge | Kgs | 7 |  |  |  |  |  |
| d | Shut Off Valve Set | Nos. | 1 |  |  |  |  |  |
| e | Liquid Line Moisture Indicator | Nos. | 1 |  |  |  |  |  |
| f | Expansion Valve | Nos. | 1 |  |  |  |  |  |
| 4 | AIR DISTRIBUTION SYSTEM |  |  |  |  |  |  |  |
|  | Aluminum DUCTING (Qty may vary on AHU location) |  |  |  |  |  |  |  |
|  | fabrication, installation and testing of Aluminium sheet metal ducts in accordance with the approved shop drawings complete with all accessories like valves, flanges, suspension rods. Anchor bolts, bolts & nuts, etc., |  |  |  |  |  |  |  |
| 4.1 | 20 G | Sqm | 80 |  |  |  |  |  |
| 4.2 | 22 G | Sqm | 80 |  |  |  |  |  |
| 5 | THERMAL INSULATION |  |  |  |  |  |  |  |
| 5.1 | Installation of Al.Foil faced Thermal insulation on ducts of 13mm thick closed cell nitrile rubber | Sqm | 100 |  |  |  |  |  |
| 5.2 | Installation of acoustic insulation for supply air ducts with 10mm thick open cell nitrile rubber. | Sqm | 100 |  |  |  |  |  |
| 6 | Installation of Terminal Boxes With Filter |  |  |  |  |  |  |  |
|  | Filter box in 20 swg MS powder coated suitable for following with gear operated VCD for supply air with 0.3 Micron HEPA filters with Aluminium powder coated perforated sheet |  |  |  |  |  |  |  |
| 6.1 | 610 x 610 x 300 | No | 10 |  |  |  |  |  |
| 6.2 | 300 x 300 x 300 | No | 6 |  |  |  |  |  |
| 7 | Installation of RETURN AIR RISERS |  |  |  |  |  |  |  |
| 7.1 | Powder coated riser complete with aluminum powder coated perforated sheet & filter for return air riser with volume control dampers. | Sqm | 15 |  |  |  |  |  |
| 8 | Installation of Diffuser / Grill / Damper |  |  |  |  |  |  |  |
| 8.1 | Supply air Diffusers in extruded aluminum construction with Volume control Damper | Sqm | 3 |  |  |  |  |  |
| 8.2 | Supply air Diffusers in extruded aluminum construction without Volume control Damper | Sqm | 3 |  |  |  |  |  |
| 8.3 | Installation of Extruded Aluminium Volume control dampers Low leakage type aero foil blade sections 100mm wide opposite blade operation ,blade linkage with operating gear fully enclosed and stainless steel side seal gaskets. | Sqm | 1 |  |  |  |  |  |
| 9 | Installation of FIRE / SMOKE DAMPER |  |  |  |  |  |  |  |
| 9.1 | Installation of GI 16g construction Fire Dampers with extended shaft for actuator mounting. The fire damper are rated for 90 minutes with fusible link designed to melt at 70°C. | Sqm | 1 |  |  |  |  |  |
| 9.2 | Installation of fusible link for above fire dampers. | No | 2 |  |  |  |  |  |
| 10 | Installation of condensate Drain piping 10 RMT per Air Handling unit |  |  |  |  |  |  |  |
| 10.1 | Drain piping using water quality blue HDPE pipe with GI fittings 32mm with 6mm thick nitrile rubber insulation | mtr | 20 |  |  |  |  |  |
| 9.1 | Drain piping using water quality blue HDPE pipe with GI fittings 32mm with 6mm thick nitrile rubber insulation | Rmtr | 15 |  |  |  |  |  |
| 11 | Installation of Remote push button stations |  |  |  |  |  |  |  |
| 11.1 | Remote push button stations consisting of one no. ON and one no.OFF illumiinated type push buttons housed in a MS box and having SS top cover plate | No. | 2 |  |  |  |  |  |
| 12 | Thermostat | No | 2 |  |  |  |  |  |
| E | MISCELLANEOUS ITEMS |  |  |  |  |  |  |  |
| 13 | Magnahelic Guage in core areas with MS powder coated box with SS 304 Flush cover | No | 6 |  |  |  |  |  |
| 14 | Magnahelic Guage for AHU across each filter | No | 4 |  |  |  |  |  |
| 15 | M.S Angle work for support if required | KG | 500 |  |  |  |  |  |
| 16 | TESTING, COMMISSIONING & VALIDATION charges |  |  |  |  |  |  |  |
| 16.1 | DQ, IQ, OQ, & PQ with necessary drawings, data sheets, certificate & maintenance manual | Set | 1 |  |  |  |  |  |
| 16.2 | Duct leak & Pressure test as per SMACNA | set | 1 |  |  |  |  |  |
| 16.3 | 1) Air balancing 2) Pressure balancing 3) Filter integrity test (DOP) 4) Particle count 5) Recovery test 6) Flow pattern test | Set | 1 |  |  |  |  |  |
| GRAND TOTAL |  |  |  |  |  |  |  |  |

*Actual quantity is taken against installation and measurement

Seal and Signature of the bidder

BILL OF QUANTITIES – INSTALLATION OF ELECTRICAL ITEMS

| SL NO | Item | Unit of Measurement (UOM) | Qty | INSTALLATION |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Base Rate | Basic Amount | Service tax (specify applicable Service Tax) | Work Contract Tax (specify applicable WCT) | Amount |
| a | b | c | d | e | F= (d*e) | g | h | I= (f+g+h) |
| 1 | Fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required. |  |  |  |  |  |  |  |
| a | 8 way (4 + 36), Double door (Main DB) | No | 2.00 |  |  |  |  |  |
| 2 | Fixing of Cable End Termination Box of sheet steel, dust protected, duly powder painted, suitable for surface mounting, vertical type, 8 Way TPN MCB | No | 2.00 |  |  |  |  |  |
| 3 | Fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  |  |  |  |  |
| a | 4 way (4 + 12), Single door (LDB) | No | 1.00 |  |  |  |  |  |
| 4 | Fixing of Cable End Termination Box of sheet steel, dust protected, duly powder painted, suitable for surface mounting, vertical type, 4 Way TPN MCB | No | 1.00 |  |  |  |  |  |
| 5 | Fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |  |  |  |
| a | 63 amps (Main DB) | No | 2.00 |  |  |  |  |  |
| 6 | Fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |  |  |  |
| a | 40 amps (LDB) | No | 1.00 |  |  |  |  |  |
| 7 | Fixing Single Pole (SP) MCB "C" Curve in the existing MCB DB complete with connections, testing and commissioning etc. as required |  |  |  |  |  |  |  |
| a | 6 amps | No | 16.00 |  |  |  |  |  |
| b | 20 amps | No | 16.00 |  |  |  |  |  |
| c | 32 amps | No | 4.00 |  |  |  |  |  |
| 8 | Fixing of Triple Pole (TP) MCB "C" Curve in the existing MCB DB complete with connections, testing and commissioning etc. as required |  |  |  |  |  |  |  |
| a | 20 amps | No | 4.00 |  |  |  |  |  |
| b | 32 amps | No | 5.00 |  |  |  |  |  |
| c | 40 amps | No | 1.00 |  |  |  |  |  |
| 9 | Fixing of single pole blanking plate in the existing MCB DB complete etc. as required. | No | 20.00 |  |  |  |  |  |
| 10 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required. (Two light points are controlled by ONE Switch & ONE 5/6 Amps Socket with ONE SWITCH) | No | 40.00 |  |  |  |  |  |
| 11 | Fixing of following size/ modules, GI / PVC box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  |  |  |  |  |
| a | 2 Module | No | 8.00 |  |  |  |  |  |
| b | 3 Module | No | 16.00 |  |  |  |  |  |
| c | 4 Module | No | 12.00 |  |  |  |  |  |
| d | 6 Module | No | 15.00 |  |  |  |  |  |
| e | 8 Module | No | 6.00 |  |  |  |  |  |
| 12 | Fixing of following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  |  |  |  |  |
| a | 5/6 amps switch | No | 40.00 |  |  |  |  |  |
| b | 15/16 amp switch | No | 5.00 |  |  |  |  |  |
| c | 3 pin 5/6 amp socket outlet | No | 15.00 |  |  |  |  |  |
| d | 6 pin 15/16 amp socket outlet | No | 5.00 |  |  |  |  |  |
| e | RJ 11 Telephone socket outlet | No | 4.00 |  |  |  |  |  |
| f | RJ 45 CAT 6 Data Socket Outlet | No | 4.00 |  |  |  |  |  |
| 13 | Wall Mounting, Single Door PVC Telephone Krone Junction Box for the termination of 10 Pair Telephone Cable with 10 pair Connection Module etc. as required. | No | 1.00 |  |  |  |  |  |
| 14 | Fixing of 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | No | 10.00 |  |  |  |  |  |
| 15 | Fixing of 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | No | 4.00 |  |  |  |  |  |
| 16 | Wiring for circuit/submain wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in existing surface/recessed medium class PVC conduit as required. |  |  |  |  |  |  |  |
| a | 2X1.5 sq.mm + 1X1.5 sq.mm earth wire | Rmtr | 500.00 |  |  |  |  |  |
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Rmtr | 250.00 |  |  |  |  |  |
| c | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | Rmtr | 250.00 |  |  |  |  |  |
| 17 | Drawing following pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  |  |  |  |  |
| a | 2 Pair | Rmtr | 300.00 |  |  |  |  |  |
| b | 10 Pair | Rmtr | 50.00 |  |  |  |  |  |
| 18 | Drawing CAT 6 UTP Cable in the existing surface/ recessed steel/ PVC conduit as required. | Rmtr | 100.00 |  |  |  |  |  |
| 19 | Fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  |  |  |  |  |
| a | 20 mm | Rmtr | 250.00 |  |  |  |  |  |
| b | 25 mm | Rmtr | 300.00 |  |  |  |  |  |
| c | 32 mm | Rmtr | 200.00 |  |  |  |  |  |
| 20 | Laying of one number PVC insulated and PVC sheathed / XLPE Armoured power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. |  |  |  |  |  |  |  |
| a | 2 X 1.5 sq. mm | Rmtr | 50.00 |  |  |  |  |  |
| b | 3 X 4 sq. mm | Rmtr | 30.00 |  |  |  |  |  |
| c | 4 X 6 sq.mm | Rmtr | 30.00 |  |  |  |  |  |
| d | 4 X 10 sq. mm (22mm) | Rmtr | 20.00 |  |  |  |  |  |
| e | 4 X 16 sq. mm (25mm) | Rmtr | 50.00 |  |  |  |  |  |
| f | 3 1/2 X 35 sq. mm (28mm) | Rmtr | 100.00 |  |  |  |  |  |
| 21 | Making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  |  |  |  |  |
| a | 2 X 1.5 sq. mm | No | 6.00 |  |  |  |  |  |
| b | 3 X 4 sq. mm | No | 4.00 |  |  |  |  |  |
| c | 4 X 6 sq.mm | No | 4.00 |  |  |  |  |  |
| d | 4 X 10 sq. mm | No | 2.00 |  |  |  |  |  |
| e | 4 X 16 sq. mm | No | 2.00 |  |  |  |  |  |
| f | 3 1/2 X 35 sq. mm | No | 4.00 |  |  |  |  |  |
| 22 | Termination of one number PVC insulated Unarmoured 0.5 sq mm annealed copper conductor 10 Pair cable | No | 2.00 |  |  |  |  |  |
| 23 | Termination of CAT 6 UTP Cable | No | 8.00 |  |  |  |  |  |
| 24 | Laying Copper Wire for Earthing |  |  |  |  |  |  |  |
| a | 6 SWG | Rmtr | 250.00 |  |  |  |  |  |
| b | 10 SWG | Rmtr | 200.00 |  |  |  |  |  |
| 25 | Fixing of pre wired Box type Light Fixture with 4 Feet 2 X 18/20 W LED Tube Light provided with opal polysterene diffuser as required complete. | No | 12.00 |  |  |  |  |  |
| 26 | Fixing of pre wired Clean Room Light Fixture with 2 X 2 Feet LED Light fitting, 55 +/- 10 W (Recess Mounting) provided with opal polysterene diffuser as required complete | No | 18.00 |  |  |  |  |  |
| 27 | Fixing of pre wired Recessed mounted, Circular Down Light, LED 5 /8 W as required complete. | No | 8.00 |  |  |  |  |  |
| 28 | Fixing of pre wired Exhaust Fan, Industrial Type, 18", Single Phase, complete. | No | 2.00 |  |  |  |  |  |
| 29 | Fixing of Aluminium/PVC Louvers for Industrial Type, 18" Exhaust Fan, complete. | No | 2.00 |  |  |  |  |  |
| 30 | Fixing of pre wired Variable Frequency Drive suitable for 3 HP AHU Blower in powder coated sheet steel enclosure with ON & OFF Push Buttons, Indication Lamps for ON & OFF, Ventilation Fan and Air Inlet Louver, etc. complete | No | 1.00 |  |  |  |  |  |
| 31 | Fixing of pre wired 1.5 Ton Split AC Unit having 5 Star Rating with suitable Stabilizer, etc. complete. Outdoor Unit shall be suitably positioned at distance of 8 Mtrs away from Indoor Unit. | No | 3.00 |  |  |  |  |  |
| 32 | Fixing of pre wired 3.0 Ton Casset Type AC Unit having 5 Star Rating with suitable Stabilizer, etc. complete. | No | 2.00 |  |  |  |  |  |
| 33 | Preparation of Drawings and obtaining approvals from Statutory Authorities | LS | 1.00 |  |  |  |  |  |
| 34 | Installation of Fire Detectors |  |  |  |  |  |  |  |
| a | Photo electric type smoke detectors. | No | 16.00 |  |  |  |  |  |
| b | Rate of rise type detectors for autoclave area. | No | 2.00 |  |  |  |  |  |
| c | Fault Isolation module. | No | 2.00 |  |  |  |  |  |
| d | Response Indicators. | No | 18.00 |  |  |  |  |  |
| e | Manual call points with break glass. | No | 2.00 |  |  |  |  |  |
| 35 | Installation, Testing and commissioning of AHU Star / Delta starter Panel with cabling from starter panel to AHU Motor. The cabling considered shall be 10 rmt. | No | 1.00 |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  |  |

*Actual quantity is taken against installation and measurement

Seal and Signature of the bidder

SECTION X

CHECK LIST

| Sl. No. | Documents | Page No. | Remarks |
| --- | --- | --- | --- |
| 1 | Tender fee(in case of download)/EMD in the form of DD from a scheduled bank drawn in favor of HLL Lifecare Limited, Payable at Thiruvananthapuram |  |  |
| 2 | Copy of Receipt of payment against the purchase of tender document/ DD from a scheduled bank against the purchase of tender document (in case purchased from HLL Office) |  |  |
| 3 | Market standing certificate to prove that the bidder manufactures the quoted items for the past THREE years |  |  |
| 4 | Duly attested copy of sales tax registration certificate |  |  |
| 5 | Duly attested copy of document to prove the legal status, place of registration and principal place of business of the undertaking |  |  |
| 6 | Copy of Balance sheet for the past three financial years, duly certified by a chartered accountant |  |  |
| 7 | Copy of Profit & Loss Account for three years certified by chartered accountant |  |  |
| 8 | Duly filled proforma showing general informations as per section VI |  |  |
| 9 | Proforma for Performance Statement (for a period of last THREE years) as per Section VII |  |  |
| 10 | Self attested statement showing financial capability necessary to perform the Contract |  |  |
| 11 | Self attested statement showing technical and production capability necessary to perform the Contract as per Section VII |  |  |
| 12 | Client's Certificate |  |  |
| 13 | Product brochure literature, write up etc. |  |  |
| 14 | Item-by-item commentary (compliance statement) on the Purchaser’s Technical Specifications demonstrating substantial responsiveness of the goods and services to those specifications or a statement of deviations and exceptions to the provisions of the Technical Specifications |  |  |
| 15 | The letter of authorization indicated by written power-of-attorney |  |  |
| 16 | Documentary evidence of constitution of firm such as Memorandum of Articles, Partnership Deed, etc., with details of Name, Address, Tel. No., Fax No., E-mail Address of firm and the Managing Director / Partner / Proprietor |  |  |
| 17 | Annual turnover statement for last three years certified by the Auditor |  |  |
| 18 | List of items quoted (without prices) |  |  |
| 19 | Copy of Format for Requisition of site visit |  |  |
| 20 | Duly attested copy of Kerala VAT registration certificate |  |  |

SECTION XI – LAYOUTS