## TENDER FOR SUPPLY AND INSTALLATION OF UPS

## FOR

## ART–IVF CENTRE AT IMCH, MEDICAL COLLEGE HOSPITAL, KOZHIKODE, KERALA

PHASE- II

### IFB NO: HLL/AFT/TDG/IVF-II/UPS/2014-15/12

HLL LIFECARE LIMITED

(A GOVT. OF INDIA ENTERPRISE)

AKKULAM  FACTORY, SREEKARIAM  P.O.

THIRUVANANTHAPURAM – 17

Phone +91 471 244 5930, Fax +91 471 244 5935

Email: tradingpaft@lifecarehll.com

Web: www.lifecarehll.com

SECTION I

## TENDER NOTICE

## HLL Lifecare Limited hereby invites sealed bids (under Two Bid system) from eligible bidders for the supply, installation and commissioning of 8 KVA UPS on turnkey basis at Institute of Maternity and Child Health, Medical College Hospital, Kozhikode, Kerala.

| SI. No | Name of the item | Name of the hospital | Qty | EMD amount in Rs |
| --- | --- | --- | --- | --- |
| 1 | 8 KVA Online UPS | IMCH, Medical College Hospital Kozhikode, Kerala | 1 | Rs. 3,000/- |

INSTRUCTION TO BIDDERS

A.INTRODUCTION

1. Eligible Bidders

  - Only primary manufacturers / authorized dealers are eligible to participate in the tender.

1.2 	Bidders should not be associated with the purchaser for the preparation of the design, specifications, and other documents used for the procurement of the equipment under this Invitation of Bids.

1.3 	The bidder should have a minimum 3 years’ experience in the field of manufacture and/or supply of UPS.

1.4 	Bidder should have good financial background.

| Sl. No. | Minimum Eligibility criteria | Narrations Other than Tender No. |
| --- | --- | --- |
| 1 | Experience | - Should have a minimum of 3 years’ experience in in supplying, installing and commissioning of UPS. |
| 2 | Licenses/Registrations for undertaking, supply and installation contracts | - Primary manufactures who participate in the tender must produce their valid manufacturing license. - Tenderers, other than manufacturers, who participate in this tender must produce the followings: - An authorization letter from Manufacturer’s / authorized distributors to participate in this tender. - Manufacturer’s manufacturing license/ Distributor appointment letter to do the business in Kerala. - Item wise Technical compliance sheet to match the technical specification prescribed in this tender. |
| 3 | Quality Certifications | Should have necessary valid Quality/System Certifications as applicable – to match technical specifications/ requirements of the item as in the tender. |
| 4 | Good financial capability necessary to perform the Contract | Supporting documents |

2. (a) LAST DATE AND TIME FOR RECEIPT OF BIDS IS 20/07/2015, AT 14.00 HRS

(b) TIME AND DATE OF OPENING OF BIDS IS 	20/07/2015, AT 15.30 HRS

B. THE BIDDING DOCUMENTS

3. Contents of Bidding Documents

3.1 	The equipment required, bidding procedures and contract terms are prescribed in the Bidding documents.

3.2 	The Bidder is expected to examine all instructions, forms, terms and specifications in the Bidding Documents. Failure to furnish all information required by the Bidding Documents or submission of a bid not substantially responsive to the Bidding Documents in every respect will be at the Bidder’s risk and may result in rejection of its bid.

4. Clarification of Bidding Documents

4.1  	A prospective Bidder requiring any clarification of the Bidding Documents may notify the Purchaser in writing at the Purchaser’s mailing address indicated in the Invitation for Bids. The Purchaser will respond in writing to any request for clarification of the Bidding Documents which it receives not later than 5 days prior to the deadline for submission of bids prescribed by the Purchaser. Written copies of the Purchaser’s response (including an explanation of the query but without identifying the source of enquiry) will be sent to all prospective Bidders who have received the bidding documents.

5. Amendment of Bidding Documents

5.1  	At any time prior to the deadline for submission of bids, the Purchaser may, for any reason, whether at its own initiative or in response to a clarification requested by a prospective bidder, modify the Bidding Documents by an amendment.

C. PREPARATION OF BIDS

6. Language of Bid

6.1 	The Bid and other documents relating to the bid shall be written in the English language. Written in any other language shall be accompanied by an accurate translation in the English language. For purposes of interpretation of the Bid, the English translation shall govern.

7. Documents Comprising the Bid

Following documents and forms are to be comprised

- Tender Fee: DD for Rs. 525.00 (inclusive of tax) drawn in favour of HLL Lifecare Limited payable at Thiruvananthapuram is to be attached towards tender fee.

- EMD / Bid Security in form of DD, drawn in favor of HLL Lifecare Limited, payable a Thiruvananthapuram. The EMD / Bid Security shall be refunded to the non-responsive bidders within 60 days from the date of opening of Bid. The Tender received without EMD will be rejected.

- The technical specifications enclosed along with the bid document shall be confirmed by signature of the bidder/authorized signatory of the bidding firm, in all pages and authorized by official seal. The information shall be filled, wherever necessary as per the instructions given.

- Duly attested copies of licenses, sales tax registration, and documents to prove the legal status, place of registration and principal place of business of the manufacturers/authorized dealer.

- Duly attested copies of quality certificates for the products, quality system certifications as specified in technical specification. The Product catalogue/Detailed printed literature to prove the technical specification along with COMPLIANCE SHEET confirming to technical specification should be attached with offer.

- Performa for equipment and quality control, duly filled as per SECTION II

- Performance statement in the proforma under SECTION III

- Documentary evidence established in accordance with ITB Clause 1 that the Bidder is eligible to bid and is qualified to perform the contract if its bid is accepted;

j)  	Documentary evidence that the equipment and ancillary services to be supplied by the Bidder shall conform to the Bidding Documents.

k)     Duly filled Bid Form and price schedule in separate sealed envelop

8. Deleted

9.  Bid Prices

9.1    The Bidder shall indicate in the Price Schedule, the Unit Prices and Total Bid prices of the equipment it proposes to supply on turnkey basis under the Contract.

9.2    Prices indicated on the Price Schedule shall be entered separately in the following manner:

(i)    The price of the equipment, quoted ex-factory/ex-show-room/ex-warehouse, or off-the-shelf, or delivered, as applicable, including all duties and sales   tax and other taxes already paid or payable:

(a)    On components and raw material used in the manufacture or assembly of the equipment quoted ex-factory

- charges for inland transportation, insurance and other local costs incidental to delivery of the equipment to the final destination;

9.3       The Bidders separation of the price components in accordance with ITB Clause 9.2 above will be solely for the purpose of facilitating the comparison of bids by the Purchaser and will not in any way limit the Purchaser’s right to contract on any of the terms offered.

9.4     	Fixed price: Prices quoted by the Bidder shall be fixed during the Bidder’s performance of the contract and not subject to variation on any account. A bid submitted with an adjustable price quotation will be treated as non-responsive and rejected.

9.6      The Price schedule shall be kept in separate sealed envelopes.

10.  Bid Currencies

10.1    Prices shall be quoted in Indian Rupees.

11.  Documents establishing bidder’s eligibility and qualifications

11.1 	Pursuant to ITB Clause 7, the bidder shall furnish, as part of its bid, documents establishing the bidder’s eligibility to bid and its qualifications to perform the Contract if its bid is accepted.

12.  Deleted

13. Period of Validity of Bids

13.1   Price Bid shall be valid for 90 days from the date of opening of Price Bid

13.2 	In exceptional circumstances, the Purchaser may solicit the bidders consent to an extension of the period of validity. The request and the responses thereto shall be made in writing.

14. Format and Signing of Bid

14.1 	The bid shall be typed or written in indelible ink and shall be signed by the Bidder or a person(s) duly authorized to bind the Bidder to the Contract. The letter of authorization shall be indicated by written power-of-attorney accompanying the bid. All pages of the bid, except for unamended printed literature, shall be initialed by the person(s) signing the bid.

14.3    Any interlineations, erasures or overwriting shall be valid only if they are initialed by the person or persons signing the bid.

D. SUBMISSION OF BIDS

- 15. Sealing and Marking of bids

Separate bids shall be submitted for price bid and technical bids.

15.1  The bidders shall seal Technical bid   and Price bid duly marking in the separate envelopes as “TECHNICAL BID” - cover “A” and “PRICE BID” - cover “B”.  The both the envelopes (cover “A” & cover “B”) shall be placed in an outer envelope. The inner envelops and the outer envelope shall be superscribed as “Tender for UPS for IVF, Kozhikode”.

15.2  The inner and outer envelopes shall be addressed to the Purchaser at the following address:

The Joint General Manager (Materials)

HLL Lifecare Limited,  Akkulam Factory,  Sreekaryam  P.O. ,

Thiruvananthapuram -17   Phone 0471 2445930 / 2445935

Email: tradingpaft@lifecarehll.com

- The outer envelope shall bear the Invitation for bids (IFB) number, and a statement:               “SUPPLY AND INSTALLATION OF UPS TO ART-IVF (PHASE-2)  and also “DO NOT OPEN BEFORE” 15.30 Hrs. ON 20/07/2015 ”

- The inner envelope shall also indicate the name and address of the bidder to enable the bid to be returned unopened in case it is declared “late/disqualified”.

- If the inner and outer envelopes are not sealed and marked as required, the Purchaser will assume no responsibility for the bid’s misplacement or premature opening.

- Bids must be received by the Purchaser at the address specified not later than the date and time specified in the Invitation For Bid.  In the event of the specified date for the submission of bids, being declared a holiday for the Purchaser, the bids will be received up to the appointed time on the next working day.

- The Purchaser may, at its discretion, extend this deadline for the submission of bids by amending the bidding documents in which case all rights and obligations of the Purchaser and bidders previously subject to the deadline will thereafter be subject to the deadline as extended.

16. LATE BIDS

16.1    Any bid received by the Purchaser after the deadline for submission of bids prescribed by the Purchaser, will be rejected and returned unopened to the bidder.

17.  MODIFICATION AND WITHDRAWAL OF BIDS

17.1 	The bidder may modify or withdraw its bid after the bid submission, provided that written notice of the modification or withdrawal is received by the Purchaser prior to the deadline prescribed for submission of bids.

17.2     A withdrawal notice may also be sent by cable or fax, but followed by a signed confirmation copy, post-marked not later than the deadline for submission of bids.

17.3   No bid may be modified subsequent to the deadline for submission of bids.

17.4 	No bid may be withdrawn in the interval between the deadline for submission of bids and the expiration of the period of bid validity specified by the bidder in the Bid Document.

E. BID OPENING AND EVALUATION

18. Opening of Bids by Purchaser

18.1 The Purchaser will open all technical bids (Cover A), in the presence of bidder's representatives who choose to attend, at 15.30 Hrs on 20/07/2015  at the following location:

HLL Lifecare Limited,

Akkulam Factory,

Sreekaryam  P.O. ,

Thiruvananthapuram -17

hone 0471 2445930 / 2445935 Email : tradingpaft@lifecarehll.com

18.2 	The bidder’s representatives who are present shall sign a register evidencing their attendance. In the event of the specified date of bid opening being declared a holiday for the Purchaser, the bids shall be opened at the appointed time and location on the next working day.

18.3   The bidder’s names, modifications, bid withdrawals and the presence or absence of the requisite documents and such other details as the Purchaser, at its discretion, may consider appropriate will be announced at the opening. No bid shall be rejected at the bid opening time, except for late bids, which shall be returned unopened to the bidder pursuant to ITB Clause 16.

18.4  The “Price Bid” (Cover B) will be opened after evaluation of “Technical bids”                 and the date and time will be intimated to bidders whose bids are qualified and responsive.

18.5 	The purchaser will scrutinize the technical bid for compliance to the specifications and documentation requirement as per the bid document. Purchaser may depute its competent officers to the premises of the bidder qualified on the basis of technical scrutiny, for on-site evaluation of the claims made in the technical bid, if deemed appropriate on purchaser’s sole discretion. The bidders will be short-listed on the basis of responsiveness of technical bid as well as report of on-site technical evaluation. The price bid of the bidders who are disqualified at the technical scrutiny and on-site evaluation will be returned un-opened. The on-site evaluation may include the inspection of the specimen sample of the equipment. The short listed bidders will be informed about the time, date and venue of the price bid opening. The successful bidder shall be identified on the basis of lowest evaluated substantially responsive bid.

19.  CLARIFICATION OF BIDS

19.1   During evaluation of bids, the Purchaser may, at its discretion, ask the bidder for a clarification of its bid.  The request for clarification and the response shall be in writing and no change in prices or substance of the bid shall be sought, offered or permitted.

20. PURCHASER’S RIGHT TO ACCEPT  AND REJECT ANY OR ALL BIDS

20.1 	The Purchaser reserves the right to accept or reject any bid, and to annul the bidding process and reject all bids at any time prior to award of Contract, without thereby incurring any liability to the affected bidder or bidders.

21. PRELIMINARY EXAMINATION

21.1   The Purchaser will examine the bids to determine whether they are complete, whether any computational errors have been made, whether the documents have been properly signed, and whether the bids are generally in order.

21.2  Arithmetical errors will be rectified on the following basis.  If there is a discrepancy between the unit price and the total price that is obtained by multiplying the unit price and quantity, the unit price shall prevail and the total price shall be corrected. If there is a discrepancy between words and figures, the amount in words will prevail.  If the bidder does not accept the correction of the errors, its bid will be rejected.

21.3 	The Purchaser may waive any minor informality or non-conformity or irregularity in a bid, which does not constitute a material deviation, provided such a waiver does not prejudice or affect the relative ranking of any bidder.

21.4   	Prior to the detailed evaluation, pursuant to Clause ITB 22, the purchaser will determine the substantial responsiveness of each bid to the bidding documents. For purposes of these clauses a substantially responsive bid is one which conforms to all the terms and conditions of the bidding documents without material deviations. Deviations from or objections or reservations to critical provisions such as those concerning Warranty, Force Majeure, Applicable law  and Taxes and Duties  will be deemed to be material deviation. The purchaser’s determination of a bid’s responsiveness is to be based on the contents of the bid itself without recourse to extrinsic evidence.

21.5   If a bid is not substantially responsive, it will be rejected by the Purchaser and may not subsequently be made responsive by the bidder by correction of the non-conformity.

22. EVALUATION AND COMPARISON OF BIDS

22.1  The Purchaser will evaluate and compare bids previously determined to be substantially responsive.

22.2    The purchaser’s evaluation of a bid will take into account the bid price including all costs as well as duties and taxes paid or payable and price of incidental services, if any, in the manner and to the extent and in the technical specifications:

- cost of transportation, insurance and other costs incidental to the delivery of equipment; to designated delivery destination and installation and handing over the same to the Purchaser, at designated location.

22.3     The following evaluation methods will be applied:

- transportation, from factory, insurance and   incidentals.

(i) transportation, insurance and other incidentals, for delivery of equipment to the required locations mentioned. The above costs will also be considered in the bid price.

(b)     Spare parts and after sales service facilities:

The cost of the Purchaser of establishing the minimum service facilities and parts inventories, as outlined elsewhere in the bid invitation, if quoted separately, shall be added to the bid price.

23. CONTACTING THE PURCHASER

23.1     No bidder shall contact the Purchaser on any matter relating to its bid, from the time of the bid opening to the time the contract is awarded.  If the bidder wishes to bring additional information to the notice of the purchaser it should do so in writing.

23.2    Any effort by a bidder to influence the purchaser in its decisions on bid evaluation, bid comparison, or selection may result in the rejection of the bidders bid.

24. INSPECTION AND TESTS

24.1   The Purchaser or its representative shall have the right to inspect and/or to test the Equipment to confirm their conformity to the Contract at no extra cost of the Purchaser. The Technical Specifications shall specify what inspections and tests the Purchaser requires and where they are to be conducted. The Purchaser shall notify the Supplier in writing of the identity of any representatives retained for these purposes.

24.2	The inspections and test may be conducted on the premises of the Supplier or its subcontractor(s), at point of delivery and/or at the final destination, where the Supplier or its subcontractor(s), shall provide all reasonable facilities and assistance including access to drawings and production data to the inspectors at no charge to the Purchaser.

24.3	Any inspected or tested Equipment fails to conform to the specifications, the Purchaser may reject them and the Supplier shall either replace the rejected Equipment or make all alternations necessary to meet specification requirements free of cost to the Purchaser.

24.4 	The Purchasers right to inspect, test and, where necessary, reject the Equipment’ arrival in at site shall in no way be limited or waived by reason of the Equipment having previously been inspected, tested and passed by the Purchaser or its representative prior to the Equipment dispatched.

F. AWARD OF CONTRACT

25. AWARD CRITERIA

25.1 	The Purchaser will award the contract to the successful bidder whose bid has been determined to be substantially responsive and has been determined as the lowest evaluated bid, provided further that the bidder is determined to be qualified to perform the contract satisfactorily.

26. PURCHASER’S RIGHT TO VARY QUANTITIES AT TIME OF AWARD

  - The Purchaser reserves the right at the time of award of contract to increase or decrease the quantity of equipment and services originally specified in the bid document without any change in unit price or other terms and conditions within the bid validity period.

  - The quantity mentioned herein are present requirement and in case more or less quantity is required, the suppliers should be prepared to effect supply at short notice on the same terms and conditions.

- PACKING, TRANSPORTATION AND  DELIVERY

  - It shall be the responsibility of the Supplier to ensure that the equipment is packed and transported in good condition and is delivered and installed at the specified locations in good operative condition to the satisfaction of the purchaser.

- DELIVERY AND DOCUMENTS

  - Delivery destination of the UPS is at IMCH, Medical College Hospital, Kozhikode, Kerala as per unit quantity specified in the tender. Delivery of the equipment shall be made by the Supplier in accordance with the terms specified in the purchase order by the Purchaser. The documents like warranty certificate, equipment manual, test certificate and also other documents to be furnished by the supplier as specified in the purchase order, shall be accompanied with each dispatch.

29. DELAYS IN DELIVERY OF EQUIPMENT

  - Delivery of the Equipment shall be made by the Supplier within 20 days from the date of placing the Letter of Indent/Purchase Order. If at any time during performance of the Contract, the Supplier  encounters conditions impeding timely delivery of the Equipment, the Supplier shall promptly notify the Purchaser in writing of the fact of the delay, its likely duration and its cause(s). As soon as practicable after receipt of the Supplier's notice, the Purchaser shall evaluate the situation and may at its discretion extend the Supplier's time for performance, with or without penalty.

29.2 	A delay by the Supplier in the performance of its delivery obligations shall render the Supplier liable to the imposition of penalty pursuant to agreement / purchase order, unless an extension of time is agreed upon pursuant to agreement / purchase order without the application of liquidated damages.

  - If the Supplier fails to deliver any or all of the Equipment or perform the Services within the time period(s) specified in the Purchase Order, the purchaser shall, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as penalty, a sum equivalent to the percentage specified in the purchase order.

30. WARRANTY

30.1 	This warranty shall remain valid for 2 YEARS after equipment or any portion thereof as the case may be, have been delivered to and accepted at the final destination indicated in the contract.

30.2  Any major repair pointed out by the Purchaser within the warranty period shall be rectified by the Supplier from the date of intimation within a period of 2 calendar days and commission the equipment to the satisfaction of the Purchaser. Failing which the Purchaser has the right to levy penalty on the Supplier per day or part thereof for each equipment until the equipments are repaired and commissioned to the satisfaction of the Purchaser.

30.3	The Supplier shall, in addition, comply with the performance and/ or consumption guarantees specified under the contract. If for reasons attributable to the Supplier, these guarantees are not attained in whole or in part, the Supplier shall at its discretion either:

31. Comprehensive Maintenance Contract (CMC)

    - The Purchaser desires to have separately comprehensive maintenance charges for a period of 5 years after the expiry of Warranty Period, clearly indicating year wise comprehensive maintenance charges.

  - The CMC shall be quoted by the bidder as prescribed in the SECTION VIII.

  - During the CMC period, 2 preventive maintenance has to be carried out by the firm in a year (i.e) one preventive maintenance for every 6 months. The minimum gap between any two  preventive Maintenance should be atleast 150 to 180 days.

  - The firm should also attend any number of breakdown calls as and when required. All breakdown calls shall be attended to immediately and all major repairs shall be rectified within 3 calendar days from the date of intimation.

  - For the UPS, periodical preventive maintenance and breakdown calls including replacement of defective spares shall be attended by you at free of cost to maintain the 95% uptime guarantee and the maximum time permitted for restoration, during the warranty period and CMC period.

  - In the event of the downtime exceeding the prescribed maximum period, the warranty period will be accordingly extended and the effective date of commencement CMC will be shifted accordingly.

  - The bidder should ensure availability of spares for the period of atleast 8 years from the date of installation of equipment.

32      PAYMENT TERMS

32.1 	The Price of the Equipment quoted shall be inclusive of Cost, insurance, freight unless otherwise specified in the purchase order.

  - 90 % payment shall be made within 30 days from the receipt and acceptance of equipment at the specified location in Purchase Order. The balance payment of 10% shall be released only after satisfactory completion of commissioning, Installation and receipt of Final Acceptance Certificate issued by the Consignee, Warranty Certificate, and also against submission of 10% of the contract value as performance guarantee by way of DD or Bank Guarantee.

  - Test Reports (wherever applicable) are to be forwarded along with the original invoices.

32.4   Payment for Annual Comprehensive Maintenance Contract Charges:

The payment of CMC will be made on six monthly basis after satisfactory completion of each six months period, duly certified by the consignee.

33. PATENT RIGHTS

33.1	The Supplier shall indemnify the Purchaser against all third-party claims of infringement of patent, trademark or industrial design rights arising from use of the Equipment of any part thereof.

34.  INCIDENTAL SERVICES

34.1 	The supplier may be required to provide any or all of the following services, including additional services, if any, as specified.

(a) 	Performance or supervision of the on-site assembly and/or start-up of the supplied equipment

(b) 	Furnishing of tools required for assembly and/or maintenance of the supplied Equipment;

(c) 	Furnishing of detailed operations and maintenance manual for each product

(d) 	performance or supervision or maintenance and/or repair of the supplied Equipment, for a period of time agreed by the parties, provided that this service shall not relieve the Supplier of any warranty obligations under this Contract; and

(e) 	Training of the Purchaser’s Personnel, at the Supplier’s plant and/or on-site, in assembly, start-up, operation, maintenance and/or repair of the supplied Equipment.

35. CHANGE ORDERS

35.1	The Purchaser may at any time by written order given to the Supplier, make changes within the general scope of the Contract in any one or more of the following:

- drawings, designs or specifications, where Equipment to be furnished under the Contract are to be specifically manufactured for the Purchaser;

- the method of shipping.

- the place of delivery; or

- the services to be provided by the Supplier.

35.2 	If any such changes cause an increase or decrease in the cost of, or the time required for, the Supplier’s performance of any provisions under the Contract, an equitable adjustment shall be made in the Contract Price or delivery schedule, or both, and the Contract shall accordingly be amended. Any claims by the Supplier for adjustment under this clause must be asserted within thirty (30) days from the date of the Supplier’s receipt of the Purchaser’s change order.

36. CONTRACT AMENDMENTS

36.1 	No variation in or modification of the terms of the Contract shall be made except by written amendment signed by the parties.

37. ASSIGNMENT

37.1 	The Supplier shall not assign, in whole or in part, its obligations to perform under the contract, except with the Purchaser’s prior written consent.

38. LIQUIDATED DAMAGES

38.1	If the Supplier fails to deliver any or all of the Equipment or to perform the Services within the period(s) specified in the Contract, the Purchaser shall, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as liquidated damages, a sum equivalent to the percentage specified of the delivered price of the delayed Equipment or unperformed Services for each week or part thereof of delay until actual delivery or performance, up to a maximum deduction of the percentage specified if any. Once the maximum is reached, the Purchaser may consider termination of the Contract.

38.2   Penalty: At the rate of 0.5%  rate as per the various terms and conditions of this contract subject    to a maximum of 5 % of the total contract value, for delay beyond the agreed period.

39. TERMINATION BY DEFAULT

39.1	The Purchaser may, without prejudice to any other remedy for breach of contract, by written notice of default sent to the supplier, terminate the Contract in whole or part;

- if the Supplier fails to deliver any or all of the equipment within the time period(s) specified in the Contract, or within any extension thereof granted by the Purchaser, or

(b) if the Supplier fails to perform any other obligation(s) under the contract.

39.2	In the event the Purchaser terminates the Contract in whole or in part,  the Purchaser may procure, upon such terms and in such manner as it deems appropriate, Equipment or Services similar to those undelivered, and the Supplier shall be liable to the Purchaser for any excess costs for such similar Equipment. However, the Supplier shall continue the performance of the Contract to the extent not terminated.

40   FORCE MAJEURE

40.1    For purposes of this Clause “Force Majeure” means an event beyond the control of the Supplier and not involving the Supplier’s fault or negligence and not foreseeable. Such events may include, but are not limited to, acts of the Purchaser either in its sovereign or contractual capacity, wars or revolutions, fires, floods, epidemics, quarantine restrictions and freight embargoes.

40.2	If a Force Majeure situation arises, the Supplier shall promptly notify the Purchaser in writing of such conditions and the cause thereof. Unless otherwise directed by the Purchaser in writing, the Supplier shall continue to perform its obligations under the Contract as far as is reasonably practical, and shall seek all reasonable alternative means for performance not prevented by the force majeure event.

41. TERMINATION FOR INSOLVENCY

41.1 	The Purchaser may at any time terminate the Contract by giving written notice to the Supplier, if the Supplier becomes bankrupt or otherwise insolvent. In this event, termination will be without compensation to the Supplier, provided that such termination will not prejudice or affect any right of action or remedy, which has accrued or will accrue thereafter to the Purchaser.

42. RESOLUTION OF DISPUTES

42.1 	The Purchaser and the supplier shall make every effort to resolve amicably by direct informal negotiation any disagreement or dispute arising between them under or in connection with the Contract.

  - If, after thirty (30) days from the commencement of such informal negotiations, the Purchaser and the Supplier have been unable to resolve amicably a Contract dispute, either party may require that the dispute be referred for resolution to the formal mechanisms. These mechanisms may include, but or not limited to, conciliation mediated by a third Party, adjudication in an agreed national forum, and national arbitration.

  - The jurisdiction of any disputes, suits and proceeding arising out of the tender shall be only in the court of Thiruvananthapuram.

The  Joint General Manager (Materials)

HLL Lifecare Limited,

Akkulam Factory, Sreekaryam  P.O. , Thiruvananthapuram -17

Phone 0471 2445930 / 2445935 Email : tradingpaft@lifecarehll.com

SECTION II

PROFORMA FOR EQUIPMENT, TENDERER AND QUALITY CONTROL

(Please attach detailed proforma incorporating the information given below)

BID NO……………………….

DATE OF OPENING……..

NAME OF THE BIDDER:……………………………………..

- Name & Full address of the Manufacturer: ………………………………………..

……………………………………………………..

(a) PAN No              			(b). ECC Code                    ( c) IEC if applicable

(d) CST No               			(e) TIN No                           (f)   Any other details

2.	(a) Telephone No.  				Office/Factory/Works

(b) Fax No.					Office/Factory/Works

(c) e-mail address

- Location of the manufacturing factory/show room

- Whether Equipments are tested to any standard specification?  If so, copies of specifications & original test certificates should be submitted.

SECTION III

PROFORMA FOR PERFORMANCE STATEMENT

Proforma for Performance Statement (for a period of last 3 years)

IFB NO: HLL/AFT/TDG/IVF-II/UPS/2014-15/12                                            03.07.2015

Name of the firm:

| Order placed by (Full Address of Purchaser) | Order No. and Date | Description Of ordered item | Quantity of item | Value of order | Date of Completion of delivery | Remarks indicating reasons for late delivery, if any | Has the equipment been satisfactorily functioning? (Attach a certificate from the Purchaser/Consignee) |
| --- | --- | --- | --- | --- | --- | --- | --- |

## SECTION IV

TECHNICAL SPECIFICATIONS

| Sl No: | Description | Desired |
| --- | --- | --- |
| A | Rating | 8KVA |
| 1 | Make | Power One / Reillo PCI (AROS) / Numeric / Aplab / GE / Emerson / Merlin Jerin / APC. |
| 2 | Model | To be mentioned (catalogue to be attached). |
| B | Design | Rectifier & Inverter with IGBT and DSP Technology. |
| 1 | DC Bus Voltage | To be mentioned. |
| C | Input |  |
| 1 | Voltage | 400 ± 15% V, 3 Phase, 4 Wire. |
| 2 | Frequency | 45 to 55 Hz. |
| 3 | Power Factor | Minimum 0.9 |
| D | Output |  |
| 1 | Rating | 8 KVA |
| 2 | Voltage | 415V, 3Phase, 4Wire, 50Hz. |
| 3 | Static Voltage Regulation | <1%. |
| 4 | Wave Form | Pure Sine. |
| 5 | THD | Maximum 2% for linear load Maximum 6% for Non-linear load |
| 6 | Frequency | 50Hz ± 0.05% |
| 7 | Bypass Efficiency | Minimum 96% |
| 8 | Overload Capacity | 125% Load for 10 minutes. 150% Load for 1 minute. |
| 9 | Efficiency | 92% at Full Load |
| 10 | Load power factor | 0.8 |
| E | Battery |  |
| 1 | Type | Sealed Maintenance Free Rechargeable. |
| 2 | Back Up | 1 Hr (60 Mts) |
| 3 | Battery AH | Sizing Calculation to be attached. |
| 3 | Make | Exide / Panasonic / Amaron |
| 4 | Guaranty | 3 Years (Replacement). |
| F | Protections | Overload & Short Circuit. |
| 1 |  | Over Temperature. |
| 2 |  | Low Battery. |
| 3 |  | Over/Under Voltage. |
| G | Display | Control Panel with LCD Screen. |
| 1 |  | Output Voltage. |
| 2 |  | DC Voltage & Current. |
| 3 |  | Trip Indication. |
| 4 |  | Alarms with event logger. |
| 5 |  | Bypass Operation. |
| 6 |  | AC Failure. |
| H | Ventilation | Forced Air Cooling. |
| I | Communication | RS 232 & RS485 with SNMP networking facility. |
| J | Protection Level | IP 20. |
| K | Environmental |  |
| 1 | Maximum Audible Noise | <65dB (At 1 meter from unit). |
| 2 | Working Temperature | 0 to 40 degree C |
| 3 | Relative Humidity | 0 to 95% Non-Condensing. |

SECTION V

## HLL LIFECARE LIMITED

Akkulam Factory

THIRUVANANTHAPURAM-695017

IFB NO: HLL/AFT/TDG/IVF-II/UPS/2014-15/12

INDEMINITY CLAUSE

If the supplier fails to execute the order within the time prescribed for the delivery of equipment ordered or violates or infringes the existing rates as agreed to as mentioned in the supply order, the supplier shall and will indemnify the company against all loses or damages whatsoever to be incurred or sustained including the legal cost or expenses incurred by the company by reason of non-delivery of equipment at agreed quantity and rate with in the time specified in the supply order.  The company will initiate legal action if the supplier fails to execute the supply order as per the schedule in the supply order for the actual loss suffered. No quantity tolerance will be permitted in this regard unless otherwise prior approval is taken by the company before dispatching any excess quantity supplied which shall be returned back on freight to pay basis at the risk of the supplier.   Responsiveness of the Bid shall be at the discretion of HLL.

The supplier shall have no right to change the quantity stipulated in the supply order.

Bid pronounced Non Responsive by HLL shall be summarily rejected.

The decision of HLL will be final and no correspondence of this shall be entertained.

We have read and understood the above conditions and agree to abide   by the same.

PLACE:                                                                         NAME AND SIGNATURE OF THE TENDERER

DATE:                                                                                                    (WITH OFFICE SEAL)

## SECTION VI

## HLL LIFECARE LIMITED

Akkulam Factory

THIRUVANANTHAPURAM-695017

IFB NO: HLL/AFT/TDG/IVF-II/UPS/2014-15/12

#### DECLARATION

I / WE, The Bidder undertake, we shall execute, within the purview of the contract, all the activities includes; transportation, loading, unloading and other technical work for the installation of the equipment at the designated site as per the contract / purchase order, at IVF centre at IMCH, Medical College, Kozhikode, Kerala.

We confirm having read and understood all the specifications, instructions, forms, terms and conditions and other requirements of the above tender (both expressed and implied) in full and that we agree to abide by all without any deviation.

SEAL OF THE TENDERER

SIGNATURE

NAME AND ADDRESS OF TENDERER

PRICE SCHEDULE (SECTION VII)

| S. No. | Item Description | Qty | Brand/Model | Manufacturer | Ex-factory price (Basic Unit Price exclusive of all Dusties & charges) | Excise Duty |  | Sales Tax |  | Freight & Insurance |  | Unit Price inclusive of all levies & charges (ColumnNo. f+h+j+l) in Rs | Total rate (c x m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | % | Amt. | % | Amt. | FOR Delivery destination IMCH, Kozhikode |  |  |  |
|  |  |  |  |  |  |  |  |  |  | % | Amt. |  |  |
| a | b | c | d | e | f | g | h | i | j | k | l | m | n |
| 1 | 8 KVA Online UPS with Battery back up | 1 |  |  |  |  |  |  |  |  |  |  |  |

Delivery schedule : strictly within 20 days from the date of release of LOI/PO

NOTE: 1) The columns may be filled as is applicable in each case.

2) Product catalogue  along WITH COMPLIANCE SHEET confirming to technical specification should be attached with offer.

3) List of optional accessories/ spares with rate, to be attached to price bid as separate sheet

4) The bids received without indication of service tax will be treated   as inclusive.

Seal and Signature of the bidder

CMC Price Schedule (SECTION VIII)

| S. No. | Item Description | Qty | Amount in Rs. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 1st year | 2nd year | 3rd year | 4th year | 5th year |
| 1 | 8 KVA Online UPS Battery back up | 1 No. |  |  |  |  |  |

Taxes:.___________

Scope of Contract:  No of Visit during the CMC period    a) Preventive maintenance visit: 2/year  b) Break down maintenance  visit: any number as required.         “CMC” Comprehensive  maintenance Contract includes; labors,  spare  and  preventive & break down maintenance.

Note: If CMC not quoted, then bid is treated as non-responsive and will rejected.

.         The applicable  taxes should be indicated separately with percentage and amount.

The bids received without indication of service tax will be treated   as inclusive.

The above rates are applicable after successful completion of 2 years warranty period from date of installation) for 5 years.

Seal and Signature of the bidder

SECTION IX

CHECK LIST

| Sl. No. | Documents | Page No. | Remarks |
| --- | --- | --- | --- |
| 1 | Bid Security in the form of DD drawn in favor of HLL Lifecare Limited, Payable at Thiruvananthapuram |  |  |
| 2 | EMD in the form of DD drawn in favor of HLL Lifecare Limited, Payable at Thiruvananthapuram / Bank Guarantee |  |  |
| 3 | Duly attested copy of factory license/ Industrial license |  |  |
| 4 | Duly attested copy of sales tax registration certificate |  |  |
| 5 | Duly attested copy of document to prove the legal status, place of registration and principal place of business of the undertaking |  |  |
| 6 | Duly attested copies of quality certificates for the products and quality system certifications |  |  |
| 7 | Duly filled proforma showing details of Equipment, Tenderer and Quality Control as per SECTION II |  |  |
| 8 | Proforma for Performance Statement (for a period of last years) as per SECTION III |  |  |
| 9 | Client's Certificate as per Section III |  |  |
| 10 | Product brochure literature, write up etc. |  |  |
| 11 | Point-wise compliance statement on the Purchaser’s Technical Specifications with statement of deviations and exceptions, if any, to the provisions of the Technical Specifications |  |  |
| 12 | The letter of authorization indicated by written power-of-attorney |  |  |
| 13 | Spare parts and after sales service facilities in India |  |  |
| 14 | Documentary evidence of constitution of firm such as Memorandum of Articles, Partnership Deed, etc., with details of Name, Address, Tel. No., Fax No., E-mail Address of firm and the Managing Director / Partner / Proprietor |  |  |