**HLL LIFECARE LIMITED**

**AKKULAM FACTORY, SREEKARIAM P.O. THIRUVANANTHAPURAM - 17**

**Amendment (3rd) Dtd 26.06.2015 to TENDER NOTICE**

**Ref: TENDER No. HLL/AFT/TDG/ODSH/EQP/2015-16/02 DATED 25/05/2015**

Following Amendments are made in the Tender for SUPPLY AND INSTALLATION OF DIESEL GENERATORS FOR SNCU IN HOSPITALS IN ODISHA STATE.

**DOCUMENTS COMPRISING BID AMENDMENT IN SUPPLY OF 25 KVA & 50 KVA DG SET**

|  |  |  |  |
| --- | --- | --- | --- |
| **S N** | **TENDER DETAILS** | | |
| TENDER FOR SUPPLY AND INSTALLATION OF 12 NOS DIESEL GENERATORS FOR SNCU HOSPITALS IN ODISHA STATE TENDER No. HLL/AFT/TDG/ODSH/EQP/2015-16/02 DATED 25/05/2015 | | | |
| 1 | **Extension of Tender opening date** | **ORIGINAL TENDER** | (a) Last Date and Time for Receipt of Bids is 16/06/2015, AT 11.00 AM (b) Date and Time of Opening of Bid is : 16**/06**/2015, AT 11.AM |
| **AMENDED**  **DATE & TIME** | (a) Last Date and Time for Receipt of Bids is **08/07/2015**, AT 2.30 PM  (b) Date and Time of Opening of Bid is : **08/07/2015**, AT 3.PM |
| 2 | **SSI Unit Benifits** | **ORIGINAL TENDER** | **Not mentioned** |
| **ADDITION** | **Section II, Instruction to Bidders, Clause 7.1.l :**  **SSI Benefits:** SSI exceptions shall be considered subject to submission of copies of valid SSI Registration Certificate, which **specifies** excemption of Tender Fee, EMD etc **for specified item** **as well as the specific capacity** of the item in the tender. |
| 4 | **Period of Validity of Bids** | **ORIGINAL TENDER** | ITB 13.1 Bids shall be valid for One year from the date of opening of Price Bid |
| **AMENDMENT** | ITB 13.1 The Price shall be valid during pendency of the contract i.e. till the period of supply, Erection and Commissioning of DG Sets as per tender terms. |
| 5 | **1. Earthing and earthing strip**  **2. Length of exhaust piping** | **ORIGINAL TENDER** | **Not mentioned** |
| **ADDITION** | 1. Earthing and earthing strips shall be on HLL/Purchaser;s Scope  2. Tenderer shall quote 5” and 3” diameter exhaust pipe for one meter each. In case any additional quantity required, will be paid extra. |
| 6 | **Inspection and Tests** | **ORIGINAL TENDER** | **Not mentioned** |
| **ADDITION** | **GCC, Sl No. 6.5 :** DG shall be run at NO LOAD for 8 hours, check and confirm that the temperature of Lubricants and Coolants within the limit during Commissioning.  After completion of the NO LOAD trial, DG shall be loaded in steps of 25%, 50%, 100% LOAD in a span of 8 hours and also confirm the temperature of engine oil and coolants within the limit and no abnormal vibration, noise and oil leakage. |
|  | **SECTION V**  **Technical Specifications** | **ORIGINAL TENDER** | It should be CPCB, Approved Acoustic Enclosure. |
| **AMENDMENT** | It should be CPCB-II, Approved Acoustic Enclosure. |
|  | **SECTION V**  **Technical Specifications** | **ORIGINAL TENDER** | Meter, MCB with Acoustic Enclosure as per CPCB Norms |
| **DELETION** | Deleted |
|  | **SECTION V**  **Technical Specifications** | **ORIGINAL TENDER** | Water-Cooled Four Stroke Multi Cylinders |
| **AMENDMENT** | Water-Cooled Multi Stroke Multi Cylinders |
|  | **SECTION V**  **Technical Specifications: Scope of Wrok** | **ORIGINAL TENDER** | Scope of the work shall include supply, Erection, Testing and Commissioning. |
| **AMENDMENT** | Scope of the work shall include Supply, Testing and Commissioning |
|  | **SECTION V**  **Technical Specifications**  **Make:** | **ORIGINAL TENDER** | Kirloskar Electric / Ashok Leyland/Cummins/Mahindra/Equivalant |
| **AMENDMENT** | Kirloskar Green / Ashok Leyland/Cummins/Mahindra/Equivalant |
|  | **SECTION V**  **Technical Specifications: Engine** | **ORIGINAL TENDER** | Engine shall be of Radiator Cooled, Four Stroke, Multi-Cylinder conforming to relevant standards |
| **AMENDMENT** | Engine shall be of Radiator Cooled, Multi Stroke, Multi-Cylinder conforming to relevant standards |
|  | **SECTION V**  **Technical Specifications:**  **Intallation, Testing & Commissioning** | **ORIGINAL TENDER** | Supply, Installation, Testing & Commissioning of the whole system shall be in the scope of the supplier. |
| **AMENDMENT** | Supply, Testing & Commissioning of the whole system shall be in the scope of the supplier.  **Testing :** DG shall be run at NO LOAD for 8 hours, check and confirm that the temperature of Lubricants and Coolants within the limit during Commissioning.  After completion of the NO LOAD trial, DG shall be loaded in steps of 25%, 50%, 100% LOAD in a span of 8 hours and also confirm the temperature of engine oil and coolants within the limit and no abnormal vibration, noise and oil leakage. |
|  | **SECTION V**  **Technical Specifications**  **Annual Comprehensive Maintenance Contral (ACMC)** | **ORIGINAL TENDER** | Supplier has to provide service support within 8 Hours. |
| **AMENDMENT** | Supplier has to provide service support within 8 Hours through the authorized servicing party of the Generator |
|  | **SECTION V**  **Technical Specifications**  **Service Part** | **ORIGINAL TENDER** | 100% after Erection, Testing, Commissioning and Handing Over of the complete system at *11 Hospitals in Odisha State* against Performance Bank Guarantee valid for a period of ONE year. |
| **AMENDMENT** | Testing and Commissioning shall be done by the supplier at free of cost |
|  | **SECTION V**  **Technical Specifications**  **Special Conditions (Sl No. 6)** | **ORIGINAL TENDER** | The DG set shall be placed on the foundation by the supplier. Foundation shall also be done by the Supplier |
| **AMENDMENT** | The unloading of DG set shall be done by the supplier’s cost. Leading, positioning & installation shall be done by HLL/Purchaser. The supplier may submit drawing for foundation of the DG set. |
|  | **SECTION V**  **Technical Specifications**  **Special Conditions (Sl No. 8)** | **ORIGINAL TENDER** | A Competent Technical person from the supplier shall be present at the time of Trial Run and for the successful Commissioning of the DG Set. |
| **AMENDMENT** | A Competent Technical person from the supplier shall be present at the time of Testing & Trial Run and for the successful Commissioning of the DG Set |

All other terms and conditions in the tender notice and tender document remain unchanged.

**JOINT GENERAL MANAGER (MATERIALS)**