TENDER

FOR

FIRE ALARM SYSTEM & SUPPLY OF PORTABLE EXTINGUISHERS FOR THE PROPOSED PACKING FACILITY BUILDING AT BALARAMAPURAM

PART-I

TECHNICAL BID

TENDER NO. HLL/ID / 13 /17

February 2013

HLL LIFECARE LIMITED

INFRASRTUCTURE DEVELOPMENT DIVISION

## TABLE OF CONTENTS

| Description | Page No. |
| --- | --- |
| Disclaimer | 1 |
| Schedule of submission of Tender | 2 |
| Press Notice | 3 |
| Definition | 4 |
| Section-I |  |
| Brief particulars of the work | 5 |
| Notice Inviting Tender | 6 |
| Section-II |  |
| Information & Instructions for Applicants |  |
| 1. General | 9 |
| 2. Method of Application | 10 |
| 3. Final Decision making Authority | 10 |
| 4. Particulars Provisional | 11 |
| 5. Site Visit | 11 |
| 6. Tender documents | 11 |
| 7. Submission of tender documents | 11 |
| 8. Eligibility Criteria for Qualification | 13 |
| 9. Evaluation of Technical Bid | 14 |
| 10. Signing of the application and number of copies | 15 |
| 11. Sealing of application | 15 |
| 12. Deadline and address for submission of applications | 16 |
| 13. Late applications | 16 |
| 14. Validity of applications | 16 |
| 15. Amendment of qualification document | 17 |
| 16. Withdrawal of applications | 17 |
| 17.Technical bid opening | 17 |
| 18. Price bid opening | 18 |
| 19. Award criteria | 18 |
| 20. Employer’s right | 18 |
| 21. Jurisdiction | 18 |
| SECTION-III |  |
| LETTER OF TRANSMITTAL | 19 |
| Form A | 20 |
| Form B | 21 |
| Form C | 23 |
| Form D | 23 |
| Form E | 24 |
| Form F | 24 |
| Technical specification | 25 |

DISCLAIMER

HLL Lifecare Ltd, India (HLL) has prepared this document to give interested parties background information on the Project. While HLL Lifecare Limited have taken due care in the preparation of the information contained herein and believe it to be accurate, neither HLL Lifecare Ltd, any of its authorities or agencies nor any of their respective officers, employees, agents or advisors gives any warranty or make any representations, express or implied as to the completeness or accuracy of the information contained in this document or any information which may be provided in association with it.

The information is not intended to be exhaustive. Interested parties are required to make their own enquiries and respondents will be required to confirm in writing that they have done so and they do not rely on the information in responding to the tender. The information is provided on the basis that it is non – binding on HLL Lifecare Limited, any of its authorities or agencies or any of their respective officers, employees, agents or advisors.

No reimbursement of cost of any type will be paid to persons or entities applying to the tender.

SCHEDULE FOR SUBMISSION OF APPLICATION

| EVENT | DATE |
| --- | --- |
| Starting date of sale of documents | 19.02.2013 |
| Last date of sale of documents | 05.03.2013 |
| Last date and time for submission of completed Tender | 05.03.2013 at 3.00 pm |
| Date and time for Opening of Technical Bid | 05.03.2013 at 3.30 pm |

The tender documents can be downloaded from the web site www.lifecarehll.com and the cost of tender document of Rs. 1040/- (Rupees One thousand and Forty only) shall be submitted along with the tender in the form of DD taken in favour of HLL Lifecare Limited payable at Thiruvananthapuram.

The completed Tender should be submitted before the due date and time of submission at the following address.

Deputy General Manager (Technical)

HLL Lifecare Limited,

Infrastructure Development Division,

“Adarsh”, T.C 6/1718(1),

Vettamukku, Thirumala PO,

Thiruvananthapuram- 695 006.

Phone - 0471 2365872/ 73

Fax	 - 0471 2368144

HLL LIFECARE LIMITED

(A GOVT. OF INDIA ENTERPRISE)

PRESS NOTIFICATION

HLL Lifecare Limited invites sealed open tenders on item rate basis from experienced, reputed Agencies satisfying the eligibility conditions for the following work for and on behalf of HLL Lifecare Limited.

| Name of Work | Estimated cost | EMD | Other details |
| --- | --- | --- | --- |
| Fire Alarm System & Supply of Portable Extinguishers for the proposed Packing Facility Building at Balaramapuram | Rs. 15,20,000/- | Rs. 30,400 | Completion period : One month Start date of Sale of documents : 19.02.2013 Last date of submission of bid : 05.03.2013 at 3.00 PM Date of Opening of technical bid : 05.03.2013 at 3.30 PM |
| The tender documents can be downloaded from the HLL web site www.lifecarehll.com and the cost of tender document of Rs. 1040/- (Rupees One thousand and Forty only) shall be submitted along with the tender in the form of DD taken in favour of HLL Lifecare Limited payable at Thiruvananthapuram. Deputy General Manager (Technical) |  |  |  |

DEFINITIONS

“APPLICANT” means a reputed Indian firm having the required experience who has purchased the tender document and applied for the same.

“APPLICATION” means the Tender document submitted by an Applicant interested in the Project in the prescribed format

“HLL” means HLL Lifecare Limited has invited the Tender.

“EMPLOYER” means the HLL Lifecare Limited, (HLL)

“YEAR” means “Financial Year” unless stated otherwise

SECTION I

BRIEF PARTICULARS OF THE WORK

- Salient details of the work for which Tender is invited is as under:

| Name of work | Estimated cost | Period of completion |
| --- | --- | --- |
| Fire Alarm System & Supply Portable Extinguishers for the proposed Packing Facility Building at Balaramapuram | Rs. 15,20,000/- | 1 month |

- The site is situated at Balaramapuram, Thiruvananthapuram.

The scope of the work: The Scope of work covers Fire Alarm System & Supply Portable Extinguishers for the proposed Packing Facility Building at Balaramapuram in accordance with drawings and specifications prepared under the direction and to the satisfaction of the HLL.

HLL LIFECARE LIMITED

(A GOVT. OF INDIA ENTERPRISE)

NOTICE INVITING TENDER

- Tenders are invited from contractors for Fire Alarm System & Supply of Portable Extinguishers for the proposed Packing Facility Building at Balaramapuram

- The work is estimated to cost is Rs. 15,20,000/- approximately. The estimate however, is given merely as a rough guide.

- Agreement shall be drawn with the successful tenderer and all the volumes of the tender document shall form part of the contract.

- The time allowed for carrying out the work will be 1 month from the date of issue of letter of Acceptance (LOA) or from the first day of handing over the site, whichever is later, in accordance with the phasing, if any, indicated in the tender documents.

- Intending tenderers should inspect the site and make judicious assessment.

- The tender documents can be downloaded from the web site www.lifecarehll.com and the cost of tender document of Rs. 1040/- (Rupees One thousand and Forty only)  shall be submitted along with the tender in the form of DD taken in favour of HLL Lifecare Limited payable at Thiruvananthapuram failure of which the tender will be rejected.

- Tenders, which should be placed in sealed envelopes, as prescribed in Para 11 of Section II (Information & Instructions to Tenderers), will be received by the Deputy General Manager (Technical), HLL Lifecare Limited, Thiruvananthapuram upto 3.00 PM on 05.03.2013. The Technical Bid will be opened by him or his authorized representative in his office on the same day at 3.30 PM.

- Earnest Money of Rs. 30,400/- in the form of a Demand Draft of a scheduled bank issued in favour of HLL Lifecare Limited, Thiruvananthapuram, or in the form of an irrevocable guarantee bond of any scheduled bank or State Bank of India, which should be placed in a separate sealed cover marked “Earnest Money” shall be submitted along with the tenders.

- Prospective applicants may request clarification regarding the Tender document on or before the last date of sale of documents. No request for clarification will be considered after.

- The contractor shall be required to deposit an amount equal to 5% of the tendered value of the work as performance guarantee in the form of an irrevocable guarantee bond of any scheduled bank or State Bank of India in accordance with the form prescribed within 30 days of issue of letter of acceptance or 15 days from the date of handing over of site whichever is later.

- The scope of the work is for Fire Alarm System & Supply Portable Extinguishers for the proposed Packing Facility Building at Balaramapuram

- Tenderers are advised to inspect and examine the site and its surroundings and satisfy themselves before submitting their tenders as to the form and the nature of the site, the means of access to the site, the accommodation they may require and in general shall themselves obtain all necessary information as to risks, contingencies and other circumstances which may influence or affect their tender. A tenderer shall be deemed to have full knowledge of the site whether he inspects or not and no extra charges consequent on any misunderstanding or otherwise shall be allowed. The tenderer shall be responsible for arranging and maintaining at his own cost all materials, tools & plants, water, electricity, access, facilities for workers and all other services required for executing the work unless otherwise specifically provided for in the contract documents. Submission of a tender implies that the tenderer has read this notice and all other contract documents and has made himself aware of the scope and specifications of the work to be done, local conditions and other factors having a bearing on the execution of the work.

- HLL Lifecare Limited does not bind itself to accept the lowest or any other tender and reserves to itself the authority to reject any or all the tenders received without assigning any reason. All tenders in which any of the prescribed condition is not fulfilled or any condition including that of conditional rebate is put forth by the tenderer, shall be summarily rejected.

- Canvassing whether directly or indirectly, in connection with tenders is strictly prohibited and the tenders submitted by the contractors who resort to canvassing will be liable for rejection.

- HLL Lifecare Limited does not bind itself to accept the whole or any part of the tender and the tenderer shall be bound to perform the same at the rates quoted. The firm or contractor shall not be permitted to tender for work in case his near relative (s) (directly recruited or on deputation in HLL) is/are posted in any capacity either non-executive or executive employee. The contractor shall also intimate the names of persons who are working with him in any capacity or are subsequently employed by him and who are near relative to any executive employee/ gazetted officer in the HLL.

- No Engineer of Gazetted rank or other Gazetted Officer employed in engineering or administrative duties in an Engineering Department of the Government of India/State Government or PSU’s  is allowed to work as a contractor for a period of two years after his retirement from Govt. service, without previous permission of the Govt. of India or HLL in writing. This contract is liable to be cancelled if either the contractor or any of his employees is found any time to be such a person who had not obtained the permission of the Govt. of India/State Government or PSU’s as aforesaid before submission of the tender or engagement in the contractor’s service.

- The tender for the work shall remain open for acceptance for a period of 120 days from the date of opening of the tenders. If any tenderer withdraws his tender before the said period or issue of letter of acceptance/intent, whichever is earlier, or, makes any modifications in the terms and conditions of the tender which are not acceptable to the HLL, then the HLL shall, without prejudice to any other right or remedy, be at liberty to forfeit 50% of the said earnest money as aforesaid.

- This Notice Inviting Tender shall form a part of the Contract Document. In accordance with clause 1 of the contract, the letter of acceptance shall be issued first in favour of the successful Tenderer/Contractor. On such communication of acceptance, the successful Tenderer/Contractor shall, within 30 days from such date, formally sign the agreement consisting of:-

a) The Notice Inviting Tender, technical bid, GCC, specifications and drawings, forming part of the tender, and, as issued at the time of invitation of tender and acceptance thereof together with any correspondence leading thereto.

b) Agreement signed on non-judicial stamp paper as per Proforma annexed to the tender document.

Deputy General Manager (Technical)

HLL Lifecare Limited

SECTION II

# INFORMATION & INSTRUCTIONS FOR APPLICANTS

  - General:

  - Letter of transmittal and forms for Technical Evaluation are given in Section III.

  - All information called for in the enclosed forms should be furnished against the relevant columns in the forms. If for any reason, information is furnished on a separate sheet, this fact should be mentioned against the relevant column. Even if no information is to be provided in a column, a “nil” of “no such case” entry should be made in that column. If any particulars/query is not applicable in case of the applicant, it should be stated as “not applicable”. The applicants are cautioned that not giving complete information called for in the application forms or not giving it in clear terms or making any change in the prescribed forms or deliberately suppressing the information may result in the applicant being summarily disqualified. Applications made by telegram or telex and those received late will not be entertained.

  - The application should be neatly type-written in English. The applicant should sign each page of the application.

  - Overwriting should be avoided. Correction, if any, should be made by neatly crossing out, initialing, dating and rewriting. Pages of the qualification document are numbered. Additional sheets, if any added by the contractor, should also be numbered by him. They should be submitted as a package with signed letter of transmittal.

  - References, information and certificates from the respective clients certifying suitability, technical know how or capability of the applicant should be signed by the autherised signatory of the client.

  - The applicant may furnish any additional information, which he thinks is necessary to establish his capabilities to successfully complete the envisaged work. He is, however, advised not to furnish superfluous information. No information shall be entertained after submission of pre-qualification document unless it is called for by the Employer.

  - Any information furnished by the applicant found to be incorrect either immediately or at a later date, would render him liable to be debarred from tendering/taking up of work in Hindustan Latex Limited.

  - Prospective applicants may request clarification regarding the Tender document on before the last date of sale of documents specified in the “SCHEDULE FOR SUBMISSION OF APPLICATION”. Any clarification given by the Employer will be posted in the web sites of HLL. No request for clarification will be considered after.

  - Joint Venture firms are not allowed to participate in the tender.

2.0  Method of Application:

  - If the applicant is an individual, the applicant shall affix his signature above his name type written in full along with his current address.

  - If the applicant is a proprietary firm, the application shall be signed by the proprietor above his name type written in full along with the full name of his firm and its current address.

  - If the applicant is a firm in partnership, the application shall be signed by all the partners of the firm above their full type-written names and current addresses or alternatively by a partner holding power of attorney for the firm. In the latter case a certified copy of the power of attorney should accompany the application. In both cases a certified copy of the partnership deed and current address of all the partners of the firm should accompany the application.

  - If the applicant is a limited company or a corporation, the application shall be signed by a duly authorized person holding power of attorney for signing the application accompanied by a copy of the power of attorney. The applicant should also furnish a copy of the Memorandum of Articles of Association duly attested by a Public Notary.

3.0 Final Decision Making Authority.

The employer reserves the right to accept or reject any application and to annul the qualification process and reject all application at any time, without assigning any reason or incurring any liability to the applicants.

4.0 Particulars Provisional

The particulars of the work given in Section I are provisional. They are liable to change and must be considered only as advance information to assist the applicant.

5.0 Site Visit

The applicant is advised to visit the site of work, at his own cost, and examine it and its surroundings by himself, collect all information that he considers necessary for proper assessment of the prospective assignment.

6.0 TENDER DOCUMENTS

6.1 The tender documents consisting of the following documents

- Part-I- Technical Bid

- Part-II – General Conditions of Contract

- Part-III- Specification, Drawings, BOQ and Price Bid

6.2 The tenderer is expected to examine carefully all the contents of the tender documents including instructions, conditions, forms, terms etc. and take them fully into account before submitting the offer. Failure to comply with the requirements as detailed in these documents shall be at the tenderer’s own risk.

7.0 SUBMISSION OF THE TENDER DOCUMENTS

The tender document shall be submitted in two parts

1. Part- I- Technical Bid

2. Part-II- Price Bid

7.1 Part –I Technical Bid shall consisting of the following,

- Earnest Money Deposit

Earnest Money Deposit, as detailed in clause 8 of NIT in original, placed in a separate sealed envelope and duly marked “Earnest Money Deposit”.

- Power of Attorney

Attested copy of Power of Attorney (in favour of the authorized signatory of the tenderer) to submit the tender.

c. Signed copies of Technical Bid, General Conditions of Contract &     Drawings.

d. Letter of transmittal

The applicant should submit the letter of transmittal attached with this document.

e. Financial information

Applicant should furnish the Annual financial statement for the last three years (in Form “A”)

f. Experience in works /similar works

Applicant should furnish the following:

    - List of all works of similar class successfully completed during the last three years (in Form “B”).

    - List of the projects under execution or awarded (in Form “C”).

    - Particulars of completed works and performance of the applicant duly authenticated/certified by an officer not below the rank of Executive Engineer or equivalent should be furnished separately for each work completed or in progress (generally as in Form “D”).

- Organization information

Applicant is required to submit the following information in respect of his organization (in Form “E”).

- Name & Postal Address, Telephone & Fax Number etc.

- Copies of original documents defining the legal status, place or Registration and principal places of business:

- Valid VAT/Works Contract Tax registration with Sales Tax Department.

- Names & Title of Directors and Officers to be concerned with the work, with designation of individuals authorized to act for the organization.

- Information on any litigation in which the applicant was involved during the last five years, including any current litigation.

- Authorization for employer to seek detailed references.

- Details & Expertise of the Applicants

- Specification & Design Data

  - Part –II Price Bid shall consisting of the following

  - Completed Price bid

8.0 ELIGIBILITY CRITERIA FOR QUALIFICATION

The tenderers who meet the following criteria only shall be considered for price bid opening.

  - The contractor should confirm the list of approved make of materials specified in the Tender which they are going to use.

  - The applicant should have satisfactorily installed and commissioned under his/their own name at least one similar work costing not less than                       Rs. 12 lakhs or two similar works costing not less than Rs. 9 lakhs during last three years ending last day of the month of February 2013. Certificate of satisfactory completion/commissioning and working of the plant with date of completion, value as per final bill paid duly certified by authorized official not below the rank of Executive Engineer/ Project Manager to be enclosed. The details of the same shall be furnished in form ‘D’.

  - The firm should have an established service centre operating in Thiruvanathapuram.

  - The applicant should have sufficient manpower and resources to carry out such works.

  - The firms should be registered with Income Tax and Service Tax Authorities and copies of PAN and Service Tax Registration have to be submitted along with application.

9.0 EVALUATION OF TECHNICAL BID

9.1 The applicants will be evaluated in the   following manner:

    - The initial criteria prescribed in para 8.1 to 8.7 above in respect of experience of similar class of works completed and financial turn over etc. will first be scrutinized and the applicant’s eligibility for qualification for the work is determined.

HLL, however, reserves the right to restrict the list of qualified bidders to any number deemed suitable by it.

  - Even though an applicant may satisfy the above requirements, he would be liable for disqualification if he has:

- Made misleading or false representation or deliberately suppressed the information in the forms, statements and enclosures required in the pre-qualification document,

- Record of poor performance such as abandoning work, not properly completing the contract, or financial failures/ weaknesses etc.

- If the applicant, or any constituent partner in case of partnership firm, has been debarred/black listed or terminated for poor performance by any organization at any time or ever been convicted by a court of law, their application will be summarily rejected.

9.3  All tenderers who qualified based on Technical Bid shall be informed and their price bids shall be opened on the date and time informed by HLL. The price bids of the unqualified bidders shall be returned unopened.

10.  SIGNING OF THE APPLICATION AND NUMBER OF COPIES

  - The tenderer shall prepare one original set of the document. The tender documents (Part I- Technical bid & Part II- Price Bid) shall be stamped and signed on all pages   by the person duly authorized to sign on behalf of the Applicant. The power of attorney duly notarized and on a stamp paper authorizing the person to sign and act on behalf of the firm should be submitted.

10.2 	The completed tender shall be without alteration, overwriting, interlineations or erasures except those to accord with instructions issued by HLL or as necessary to correct errors made by the tenderer. All amendments/ corrections shall be initialed by the person/ persons signing the tender.

10.3  	An authorized representative shall have the authority to conduct all 	business and incur liabilities related thereto for and on behalf of the       	Applicant, during the process and thereafter.

## 11.0     SEALING AND MARKING OF APPLICATIONS

11.1 	The Technical and Price bids shall be sealed in two separate           envelopes,   superscribed as PART-I Technical bid and PART-II Price Bid respectively.  The two covers shall be sealed in a single large envelope and submitted on   or before the last date and time for submission of the application. The envelopes shall be titled “Fire Alarm System & Supply Portable Extinguishers for the proposed Packing Facility Building at Balaramapuram” and clearly marked in English with name of the Applicant.

  - No responsibility will be accepted by the HLL for the misplacement or premature opening of a tender, not sealed or marked as per aforesaid instructions.

## 12     DEADLINE AND ADDRESS FOR SUBMISSION OF APPLICATIONS

12.1  	Applications shall be submitted to HLL Lifecare Ltd., by hand or through registered post or courier service at the address given below and not later than 3.00 pm on 05.03.2011. In respect of Applications received by post or courier, HLL shall not assume any responsibility for any delayed delivery. Documents submitted in connection with this tender will be treated confidential.

### The Application should be addressed to

Deputy General Manager (Technical)

Infrastructure Development Division,

HLL Lifecare Limited,

“Adarsh”, T.C 6/1718(1),

Vettamukku, Thirumala PO,

Thiruvananthapuram- 695 006.

Phone - 0471 2365872 / 73

Fax	- 0471 2368144

## 12.3	HLL may, at its discretion, extend the deadline for the submission of Tender, in which case all rights and obligations of HLL and the Applicants subject to the previous deadline shall thereafter be subject to the deadline as extended.

## 13.0  LATE APPLICATIONS

Application received after the dead line of submission of Application shall not be considered or opened under any circumstances.

## 14.0    VALIDITY OF APPLICATIONS

## Application shall be valid for a period of 120 days from the last date of submission of Applications. HLL retain the right that in exceptional circumstances at its own discretion, it may ask the applicants to extend the validity of their application for a specified period. The Applicant not submitting the letter of extension of the validity period at that time shall not be further considered.

## 15.0	AMENDMENT OF TENDER DOCUMENTS

## 15.1   	At any time prior to the deadline for submission of Applications,             HLL either on its own or on request of the Applicant, may amend the Tender Documents by issuing addenda.

## 15.2    	An addendum issued shall be part of the Tender Documents and shall be informed to the bidders who have purchased the tender documents or shall be posted at the website of HLL as per the date specified in Schedule for submission of tender. The applicants are advised to check the websites specified above after the last date of issue of addendum and download the addendum issued, if any.

## To give Applicants reasonable time to take an addendum into account in preparing their Applications, HLL may, at its discretion, extend the deadline for the submission of Applications.

## 16.0   WITHDRAWAL OF TENDERS

## 16.1  	No modification or substitution of the submitted application shall be allowed.

## A tenderer may withdraw its Tender after submission, provided that written notice of the withdrawal is received by HLL before the due date for submission of Applications. In case an applicant wants to resubmit his application, he shall submit a fresh application following all the applicable conditions.

## 16.3   The withdrawal notice shall be prepared in Original only and each page of the notice shall be signed and stamped by authorized signatories. The copy of the notice shall be duly marked “WITHDRAWAL”.

17.   TECHNICAL BID OPENING & EVALUATION

17.1 	The covers containing Tender Security and Technical bid will be opened in the presence of the authorised representatives of bidder s at the date and time prescribed in the schedule of submission of Application.

## Incase the bidder’s technical submittal is found non-responsive with the qualification requirements, the same is liable to be rejected. The price bid of bidders who do not qualify based on the evaluation of technical bids shall be returned unopened.

18.0 PRICE BID OPENING

The price bid of only the qualified bidders will be opened. Evaluation of the financial offer will be based on price quoted by the contractor. Any subsequent alteration in prices shall not be given any cognizance.

19.0  AWARD CRITERIA

HLL will award, the contract to the tenderer, whose tender has been determined to be substantially responsive, complete and in accordance with the tender documents, and whose total evaluated price for undertaking the entire project as per the tender documents is the lowest.

20.0   EMPLOYER’S RIGHT TO ACCEPT AND TO REJECT ANY OR ALL          TENDERS.

  - The employer reserves the right, without being liable for any damages or  obligation to inform the applicant, to:

- Amend the scope and value of contract to the applicant.

- Reject any or all of the applications without assigning any reason.

20.2    	Any effort on the part of the applicant or his agent to exercise influence or to pressurize the employer would result in rejection of his application.  Canvassing of any kind is strictly prohibited.

### 21.0 JURISDICTION

### All disputes arising shall be subject to the jurisdiction of the appropriate court at Thiruvananthapuram, India and will be governed by the laws of India.

SECTION III

LETTER OF TRANSMITTAL

From:

To

Deputy General Manager (Tech)

HLL Lifecare Limited,

Infrastructure Development Division,

“Adarsh”, T.C 6/1718(1),

Vettamukku, Thirumala PO,

Thiruvananthapuram- 695 006.

Subject: Submission of Tender for ‘Fire Alarm System & Supply Portable Extinguishers for the proposed Packing Facility Building at Balaramapuram

Sir,

Having examined the details given in the Tender press notice and Qualification documents for the above work, I/we hereby submit the qualification document and other relevant information.

- I/We hereby certify that all the statements made and information supplied in the enclosed forms A to E and accompanying statements are true and correct.

- I/We have furnished all information and details necessary for pre-qualification and have no further pertinent information to supply.

- I/We submit the requisite certified solvency certificate and authorize HLL Lifecare Limited to approach the Bank issuing the solvency certificate to confirm the correctness thereof. I/We also authorize HLL Lifecare Limited to approach individuals, employers, firms and corporation to verify out competence and general reputation

- I/We submit the following certificates in support of our suitability, technical know-how and capability for having successfully completed the following works:

Name of work							Certificate from

Enclosures.

Seal of applicant

Date of submission					          Signature(s) of Applicant

FORM ‘A’

FINANCIAL INFORMATION

- Financial Analysis – Details to be furnished duly supported by figures in balance sheet/profit & loss account for the last three years duly certified by the Chartered Accountant. (Copies to be attached).

A.  Gross Annual turnover

Years

| 2008-09 | 2009-10 | 2010-11 |
| --- | --- | --- |

B    Profit/ loss

Years

| 2008-09 | 2009-10 | 2010-11 |
| --- | --- | --- |

- The following certificates are enclosed:

- PAN & Service Tax Registration copies

Signature of Chartered Accountant with Seal 		   Signature of Applicant

FORM ‘B’

DETAILS OF ALL WORKS OF SIMILAR CLASS COMPLETED DURING THE LAST THREE YEARS ENDING LAST DAY OF THE MONTH OF JUNE 2011

| Sl. No | Name of work/ project and location | Owner or sponsor | Cost in Crores | Date of commencement as per contract | Stipulated date of completion | Actual date of completion | Litigation /arbitration pending /in progress with details* | Name and address /telephone number of officer to whom reference may be made | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 8 | 10 |

* Indicate gross amount claimed and amount awarded by the Arbitrator.

Signature of Applicant

FORM ‘C’

# PROJECTS UNDER EXECUTION OR AWARDED

| S No | Name of work/ project and location | Owner or sponsoring organization | Cost of work in Crores | Date of commencement as per contract | Stipulated date of completion | Litigation /arbitration pending /in progress with details* | Name and address /telephone number of officer to whom reference may be made | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

* Indicate gross amount claimed and amount awarded by the Arbitrator.

Signature of Applicant

FORM ‘D’

# PERFORMANCE REPORT OF WORKS REFERRED TO IN FORM “B” & “C”

- Name of work /Project & Location

- Brief description of Nature of Work:

- Agreement No.

- Contract Value.

- Date of start

- Date of completion

    - Stipulated date of completion

    - Actual date of completion

- Amount of compensation levied for delayed completion, if any

- Amount of reduced rate items, if any.

- Performance Report

- Quality of work								Very Good/Good/Fair/Poor

- Financial soundness		  						Very Good/Good/Fair/Poor

- Technical Proficiency 							Very Good/Good/Fair/Poor

- Resourcefulness 								Very Good/Good/Fair/Poor

- General behavior 								Very Good/Good/Fair/Poor

Dated:		 					Executive Engineer or

Officer of Equivalent Grade

FORM ‘E’

# STRUCTURE & ORGANIZATION

- Name & Address of the applicant

- Telephone No./Fax No.

- Legal status of the applicant (attach copies of original

document the legal status).

  - An individual

  - A proprietary firm

  - A firm in partnership

  - A limited company or Corporation

- Particulars of registration with various Government bodies (attach attested photocopy).

Organization/Place of registration 				Registration No.

1.

2.

3.

- Names and Titles of Directors & Officers with designation to be concerned with this work.

- Designation of individuals authorized to act for the organization.

- Was the applicant ever required to suspend construction for a period of more than six months continuously after you commenced the construction? If so, give the name of the project and reasons of suspension of work.

- Has the applicant, or any constituent partner in case of partnership firm, ever abandoned the awarded work before its completion? If so, give name of the project and reasons for abandonment.

- Has the applicant, or any constituent partner in case of partnership firm, even been debarred/black listed for tendering in any organization at any time? If so, give details.

- Has the applicant, or any constituent partner in case of partnership firm, ever been convicted by a court of law? If so, give details.

- Has the applicant any valid VAT/Works Contract Tax registration with the Sales Tax Department?

- Any other information considered necessary by not included above.

Signature of Applicant

Form F

SAP VENDOR CREATION TEMPLATE

| Name of Vendor / Supplier |  |  |
| --- | --- | --- |
| Address for Communication |  |  |
| Phone Number |  |  |
| Type of Organisation |  | Company / Partnership / Proprietor |
| PAN Number [attach copies] |  |  |
| TIN Number [attach copies] |  |  |
| CST Number [attach copies] |  |  |
| Service Tax Registration No [attach copies] |  |  |
| Bank Details Name of Bank |  |  |
| Account Number |  |  |
| RTGS / NEFT [IFS] Code |  |  |
| Branch Name & Address |  |  |

Name & Signature of Contractor

TECHNICAL SPECIFICATIONS

FOR

FIRE DETECTION & ALARM SYSTEM

1.0    	TECHNICAL SPECIFICATIONS FOR FIRE DETECTION & ALARM SYSTEM

1.1    	General

Work under this subhead is time-bound and has to be completed within the time limit set in the tender. Work shall be executed in accordance with an agreed time schedule which shall be submitted by the tenderers along with their offer and agreed to by owners.

1.2 	Scope of Work

The scope of work in this subhead shall consist of furnishing all labour, materials, equipment and appliances necessary and required to completely do all work relating to the supply, installation, testing & commissioning of Fire Detection System Works ofHLL Lifecare Ltd, Balaramapuram unitas described herein after and shown on the drawings. The scope of work in general shall include the following.

- Supply Installation Testing & Commissioning of Fire Detection& Alarm System.

- Supply & Installation of Fire Extinguishers.

Without restricting to the generality of the foregoing, the work shall include all works as specified in the scope of work.

1.3	Contractor’s Experience

1.3.1	Contractors shall engaged specialist agency only for this work of Fire Fighting systems.

1.3.2	The selected specialist agency must have sufficient experience in the execution of turn-key projects as specified.

1.3.3	Contractor must submit with the tender a list of similar jobs carried out by him as required along with the name of works, name and address of clients, year of execution, capacity of plant and value of work.

1.4	Technical Information

1.4.1	Contractor shall submit along with the tender copies of detailed specifications, cuts, leaflets, and other technical literature of equipment and accessories offered by him.

1.4.2	Contractor’s attention is specially invited to the special conditions and other clauses in the agreement which required the contractor to :-

a. 	Submit detailed shop drawings.

b. 	Use material of specific makes and brands.

c. 	Obtain all approvals from Fire Fighting authorities.

d. 	Execute the entire work on a turn-key basis so as to provide a totally operating plant.

2.0	Testing

2.1	Testing on Completion of Installation

The entire system shall be tested after completion of installation as per the operating sequence specified.

2.2	Schedule of Inspection

Testing of fittings/equipments shall be carried out either at site or at works in the presence of a CLIENT/CONSULTANT’s representative given below:

1.	Fire Alarm panel		-	Inspection by Client/Consultant at

Manufacturers works

before dispatch.

2.	Fire Extinguishers		-	Visual inspection at

.					site for ISI mark.

Approvals	It shall be the responsibility of the contractor to obtain the approval of drawings and to get the installation inspected and passed by any concerned authorities, as may be necessary as per local by laws, any fee payable to the local bodies for such activities shall be reimburse by the Client/Consultant on production of receipt.

9.0	Standards and Codes

1.	IS – 1648 – 1961	Code of Practice for fire safety of 			building (general) fire fighting 			equipment and maintenance.

2.	IS – 934 – 1976	Specification for portable chemical fire 		extinguisher soda acid type.

3.	IS – 2873 – 1969	Specification for fire extinguisher for 			carbon dioxide

4.			National building code

# 3.	FIRE DETECTION AND ALARM SYSTEM

## 3.1	STANDARDS

The manufacture, identification of material and testing of equipment covered in this specification shall comply with the latest editions as on date of opening of tenders of the appropriate standards of the following.  Unless otherwise specified, Indian Standards are preferred.  All the appliances and accessories shall carry IS or International certification and shall be of approved make.

NFPA 72E Standards on automatic fire detection.

IS:2189	Code of practice for selection, installation and maintenance of automatic fire detection and alarm system.

##### IS: 823  Welding procedure

IS: 1652Batteries

IS: 694  PVC insulated cables (light duty) for working voltage upto 1100 volts.

IS: 1554 PVC insulated cables (heavy duty) for voltage upto 1100 volts.

IS: 5959Specification for polythelene insulated PVC sheathed heavy duty electric cables, voltage not exceeding 1100 V

##### IS: 5578	Guide for marking of insulated conductors

IS: 3043Code of practice for earthing.

IS: 5216Guide for safety procedures and practices in electrical work.

In case where the offer deviates from the specified standards, the tenderer shall indicate clearly in the offer the alternative standards proposed and details thereof.

Unless otherwise mentioned, all applicable codes and standards shall be of the latest editions as published by the Indian Standards and all other such as may be published by them during the tenure of the contract, and shall govern in respect of workmanship, properties of materials, installation and methods of testing.  In case where suitable Indian Standards are not available, generally accepted codes and practices as approved by CLIENT/CONSULTANT shall be adopted. Any changes or modifications directed by CLIENT/CONSULTANT shall also be incorporated by the contractor during execution of the work.

Automatic fire detection and alarm system consists of fire control panel, detectors, manual call points, hooters, isolators, response indicators, etc.  The equipment and cables of the system shall be independent of any other system in the premises and shall not be shared with any other system. The fire detection and alarm system shall be installed as per  NFPA 72E / IS-2189 code.

  - DETECTORS AND ACCESSORIES

    - Detectors

The fire detectors shall be of analogue addressable type to detect one or more characteristic of fire like smoke, heat or flame. It shall be sleek, suitable communication technique with noise immunity, built-in functional test switch, microprocessor based technology, mechanically integrated photoelectric and ionization shared volume smoke chamber, etc. All types of detectors shall be of both electronically  and manually programmable type using dip-switches or handheld programmer or from fire control panel. Reversed polarity or faulty zone wiring shall not damage the detector.  The detector shall have no moving parts of components subject to wear.  It shall be possible to test the detector in the field.  The response  of a detector shall always be clearly visible from outside by a flashing light on the base. The detector shall connect to the control unit via a fully supervised two-wire circuit. A built barrier shall prevent entry of insects into the sensor.  The detector shall be designed for fast and simple cleaning.

All electronic circuits must be solid state devices and virtually hermetically sealed to prevent their operation from being impaired by dust dirt or humidity.  All circuitry must be protected against usual electrical transients and electromagnetic interference. All radioactive parts of the source, if any,  shall be fully gold plated. The detector shall be inserted into or removed from the base by a simple push-twist mechanism to facilitate easy exchange for cleaning and maintenance.

The smoke & heat detectors shall fit into a common type standard base.  The standard base shall be supplied with a seal plate, preventing dirt, dust, condensation or water reaching the wire terminals or the detector points. Detectors shall be provided with a MS box for entry and termination of armoured cable and to protect detectors terminals.

At the time of installation and prior to commissioning, every detector shall be allotted an identification number. All detectors shall  have LED blink when it is addressed. Detectors shall not be either partially or totally recessed in ceiling or wall. Detectors shall be suitably protected where they are liable to be subjected to mechanical damage. Detectors should not be painted or coated or covered in any manner after installation as this will adversely affect the sensitive of operation.

3.2.2  Smoke detectors

It shall be of optical-cum-thermal type. Smoke detectors shall quickly respond to smoke containing small particles normally produced and heat likely to be generated and automatically adjusts sensitivity without needing operator intervention.

3.2.3  Heat detector

It shall be of fixed-cum-rate of rise temperature type.  Heat detectors shall be suitable for use in situation where sufficient heat is likely to be generated and damage caused by heat generated.

3.2.4.	Loop Hooters

The loop hooters shall be so arranged that when any alarm operates all the hooters through out the premises shall be activated. The hooters at the fire alarm shall be electronic type having frequency of suitable frequency range. The hooters shall be capable to produce a sound output of 90 db at 1 m. Hooters shall be of loop powered and no separate power is provided.

‘Fault’ alarm and ‘Fire’ alarm in a panel sounder shall be distinctly different. Fire alarm sounders shall not be used for any purpose other than for fire operations. When installed flush with a false ceiling these shall match the ceiling surface.  Necessary provisions such as wooden boxing or frame work, if required, to accommodate the sounders shall be made in the ceiling in advance.

These shall be installed at a height not lower than 2.4 m, except when recessed in a false ceiling of lower height.  In such cases the sounders shall be recessed at false ceiling level.

The panel sounders in the respective panels shall be actuated automatically as soon as fire alarm signal is initiated from any trigger device connected to them.  These shall also be sounded when there is a fault alarm signal within their areas of control.  The sound shall be continuous and of the same characteristics from all fire alarm sounders in a building.

3.2.5.	Loop Isolators

Loop isolators shall be designed to protect one area or a number of devices which are consecutively wired in a loop. Its function is to isolate a section of the loop if a problem develops within that section, allowing the remainder of devices connected on the loop to function correctly. Loop isolators shall be provided after every 20-30 devices in each loop.

3.2.6.	Manual Call Points (MCPs)

It shall be of ‘break glass’ type, and 1.5mm thick welded sheet steel or 3 mm thick cast aluminium. The front glass shall be breakable. The MCPs shall be recess mounted suitable to support the intelligent addressable panel.  It  shall form an integral part of the fire detector system. The housing shall be dust/vermin proof properly sealed with rubber lining.  The glass frangible element shall keep a push button pressed inside such that in the event of breaking the glass, the push button is released to actuate an alarm in the control panel.  MCPs shall be easily resetable with key.

Where sheet steel is used for, this shall be thoroughly cleaned off dust, dirt, grease and rust if any and two coats of anti rust primer shall be given both inside and outside.  This shall be followed by two coats of synthetic enamel paint in fire red colour on the external surface that will be visible on installation. In the case of cast aluminium body for a call box, the surface shall be neatly finished with red colour paint.   The following words shall be painted on the front of the call box in contrasting colour with a letter size of not less than 5mm.

“BREAK GLASS IN CASE OF FIRE”

Installation requirements:-

Manual call points shall be located at exit space and shall be installed at a height of 1.4 m above the floor at an easily accessible position. They shall be installed at easily accessible, well illuminated positions, preferably in a contrasting background so that they are easily noticable from either direction.  They may be semi-recessed so as to project by 10mm. They shall be installed free from obstructions.

## 3.2.7.  Fire Control Panel

The fire alarm control panel shall be of micro processor controlled and of modular hardware design of intelligent addressable type. It shall be housed in a steel enclosure. It shall also be finished with hard wear textured epoxy paint/ powder coated. Cable entries shall be provided on the top and bottom of the panel.

The system capacity shall be based on the number of devices  and control modules. Each devices in the system shall be identified by its unique address position on the two wire loop. The panel retains command over the alarm process, LED indicators, automatic test feature and  loop hooters. The panel shall be of software programmable. The panel shall be capable of:-

- programmable at site.

- automatic system test activates

- detector sensitivity adjustments

- alarm verification

- Alpha/numerical display

- Relay control module

- Support for bacnet and modbus protocol.

- maintenance alert facilities

- provision to connect to PCs

The panel shall have facility to shut off individual AHUs in case of fire through relay arrangements.  The relay shall be suitable to withstand AHU contactor coil current.

The manufacturer of fire control panel, detectors and other detection devices shall have own or authorized service centre in India with spares for carrying out maintenance service during the guarantee and maintenance periods.  The tenderer shall submit a brief write-up of the service centre facilities available in India along with the tender.

3.2.8    Power Supply of panel

The power supply shall drive the system from either the main electrical supply single phase supply or the standby power supply.  The standby power supply shall be derived from exclusive SMF back-up batteries of reputed make.  Standby power supply shall be capable of maintaining the system in normal operation having a period of not less than 24 hrs. after the failure of normal main supply.

### 3.2.9. Control Cable

The control cable for wiring fire alarm system shall be of 650 Volt grade.  Cables shall be laid as per relevant installation standards. The size of these cables are specified in schedule of requirements.

3.2.10  Cable Glands

Cable glands shall be of heavy duty single compression type of brass, chrome plated. These shall have a screwed nipple with conduit electrical thread and checknut. These shall be suitable for armoured/unarmoured cables, which is being used.

3.2.11  Cable Connectors

Cable connectors, lugs/sockets, shall be of copper/aluminium alloy, suitably tinned, solderless, crimping type. These shall be suitable for the cable being connected and type of function (such as power, control or connection to instruments, etc.)

# 4.    INSPECTION AND TESTING

# (Fire detection and alarm system)

## 4.1	INSPECTION

All materials shall be offered for inspection in cleaned condition, prior to erection.  At no event, site fabricated work /material shall be installed in position without inspection and approval by CLIENT/CONSULTANT.  The Contractor shall ensure that each stage of fabrication is carried out in compliance with the procedures specified in the IS standards as applicable and/or specified in this document.

The contractor shall conduct sample tests of all the materials supplied at reputed laboratories/agencies as directed by CLIENT/CONSULTANT at his own cost and test reports are to be submitted. Inspecting officials like CLIENT/CONSULTANT, TAC / Local Authorities shall have the right to access the premises of the work at any time with or without giving prior notice. All the formalities or procedures for conducting the inspections by the authorities as required by them shall be arranged by the contractor free of cost.

All testing shall be carried out in the presence of CLIENT/CONSULTANT/ statutory authorities and test registers shall be maintained by the contractor. The contractor shall provide all material, tools, equipment, instruments, services and personnel required to perform the tests and remove debris resulting from cleaning and after testing free of cost.

The original test certificates of all tests conducted are to be forwarded to  CLIENT/CONSULTANT.  After conducting the tests, any defects found on materials, equipment, piping, etc. shall be got rectified/repaired / replaced by the Contractor without any extra cost.

4.2	TESTING

4.2.1 Fire Detection and Alarm System

The entire fire detection and alarm system shall be tested for continuity and performance as per IS-2189 code. After installation, the visual inspection of all the detectors shall be made to make sure that they are properly installed.  Each detector shall be inspected to ensure that it is properly mounted and connected.  Heat detectors shall be tested to initiate an alarm by a heat source such as hair drier or a shielded heat lamp.  After each heat test, the detectors shall be reset.  Smoke detectors shall be tested to initiate an alarm at its installed location with smoke or other aerosol.   All detectors found to have the sensibility outside the approved range shall not be used.

Detectors, control and indicating panels, sounders shall be tested at the manufacturer’s factory and test certificate be furnished with the supply. Type test certificate to prove conformity to the relevant contract specifications shall be furnished with the supply, from recognised testing institutions or Govt. test bodies in India or abroad.

Following tests shall be conducted in the presence of CLIENT/CONSULTANT and the test certificate shall be furnished with the record of tests.

4.2.2 Continuity test

Test for insulation resistance of the wiring work and the control and indicating panels.

    - Test for system operation.

Tests for detectors shall be conducted using a test fire at normal floor level. The system operation for fault conditions shall be conducted by introducing faults such as open circuit, short circuit, removal of detector, open/short circuit in a sounder circuit etc. Tests relevant to loop isolators shall also be conducted to confirm that it functions as required.

5. 	TECHNICAL DATA

(Fire detection and alarm system)(To be submitted along wit BILL OF QUANITIES)