HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

# THIRUVANANTHAPURAM-695017

Email: materialsaft@lifecarehll.com

Website: www.lifecarehll.com

PH:  +91 471 2442641, 2445930

FAX: +91 471 2445935

### INVITATION FOR BID

(TECHNICAL BID)

# FOR

FABRICATION, SUPPLY, ERECTION AND INSTALLATION OF

SELF SUPPORTED CHIMNEY FOR FORBES MARSHAL MAKE 2 TON BOILER

Quantity: 1 Number

AT

AKKULAM FACTORY

THIRUVANANTHAPURAM – 695 017

HLL/AFT/PUR/CHIMNEY-BOILER/2013-2014                                                  19/02/2014

TENDER NOTICE

Sub:-  Fabrication, Supply, Erection and Installation of Self Supported Chimney for Forbes Marshal Make 2 Ton Boiler reg:-

Sealed and superscribed tenders under two bid system are invited from manufacture(s) / Authorized Agent(s) for the Fabrication, Supply, Erection and Installation of Self Supported Chimney for Forbes Marshal Make 2 Ton Boiler - One Number at HLL Lifecare Ltd, Akkulam Plant.

| Name of the Item | Tender No: | Date & Time of Opening of bids | Delivery |
| --- | --- | --- | --- |
| Fabrication, Supply, Erection and Installation of Self Supported Chimney for Forbes Marshal Make 2 Ton Boiler | HLL/AFT/PUR/ CHIMNEY-BOILER/2013-2014 | at 4.00 PM | 45 days (From the date of LOI/PO) |

The detailed Tender Notice and tender documents can be downloaded from our website www.lifecarehll.com. Amendments if any to this tender notice will be published only in our website.

Date of the tender opening is 06/03/2014

JGM (Mtls)

# Ph No: +91 471 2445930

# Fax No: +91 471 2445935

# Email: materialsaft@lifecarehll.com

## HLL LIFECARE LIMITED

Akkulam Factory, Sreekariyam (PO)

THIRUVANANTHAPURAM-695017

###### CONTENTS OF BIDDING DOCUMENTS

| Sl No | Schedule | Description | Page No |
| --- | --- | --- | --- |
| 1. |  | INSTRUCTION TO BIDDERS | 4-5 |
| 2. | Schedule - A | WORK CONDITIONS, DRAWING & CHIMNEY DESIGN | 6-10 |
| 4. | Schedule - B | QUESTIONNAIRE | 11-12 |
| 5. | Schedule - C | TERMS & CONDITIONS | 13-15 |
| 7. | Schedule - D | INDEMINITY CLAUSE | 16 |
| 8. | Schedule - E | DECLARATION | 17 |
| 9. | Schedule - F | PRICE BID | 19-20 |

***

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

THIRUVANANTHAPURAM-695017

HLL/AFT/PUR/CHIMNEY-BOILER/2013-2014	19/02/2014

##### I -  INSTRUCTIONS TO BIDDERS

1. The Bid is intended to procure material as per specification in Schedule A.

2. This is a two Bid system comprising of:

- Technical Bid

- Price Bid

3. Both the Bids shall be submitted in sealed covers separately.  Tender Nos. of the Technical Bid and Price Bids shall be super scribed on the respective covers in order to clearly identify between the 2 Bids.  The two separately marked Bids enclosed in a single sealed cover with the respective Tender No. mentioned thereon, complete in all respect, addressed to the The Joint General Manager (Materials)  HLL Lifecare Limited, Akkulam Factory, Trivandrum – 695017, Kerala, India should reach us on or before the due date and time mentioned in the Tender Notification.  HLL shall not be responsible for any delay.  Tender brought to the office after prescribed time will not be   accepted. HLL will not be responsible for any delay in transit of tenders sent by post.

4. Eligibility: Party should have 5 years of experience in the similar work and should have successfully completed 2 Nos of minimum 3 Mtr height chimney. (Party should submit supporting documents also for the same)

5. The technical bid should accompany an EMD the details are shown in clause 3 of schedule C.

6. In the event of the date mentioned above being declared subsequently as holiday for the purchaser’s office, the due date for submission and opening of bids will be the next working day at the same venue and time.

7. The Purchaser may, at its discretion, extend the date & time for the submission of bids by amending the bid documents in which case, all rights & obligations of the Purchaser & bidders shall the subject to the extended date & time.

8. Bids received after the deadline for submission shall not be considered.

9. The Bidder is expected to examine all specifications, Instructions, Forms, terms and conditions given in the Bidding documents.  Failure to furnish all information required in the Bidding documents or submission of a Bid not substantially responsive to the bidding documents in every respect will be at the Bidders risk and may result in rejection of the Bid. Any clarification required will have to be obtained from our office.

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

THIRUVANANTHAPURAM-695017

HLL/AFT/PUR/CHIMNEY-BOILER/2013-2014	19/02/2014

10. A Declaration as given in Schedule - E stating that ALL TERMS AND CONDITIONS of this Tender is acceptable should accompany the tender failing which the tender is likely to be summarily rejected.

11. The Price Bid of those Tenderers who qualify in the Technical Bid only will be opened.

12. Those bidders who download the tender documents from our website should furnish the Name and address of the vendor, name of contact person, telephone & Fax numbers and Email details immediately by fax/Email.

13. Any changes pertains to this tender shall be communicated only through our website www.lifecarehll.com.

Schedule – A

Page 1 of 5

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

THIRUVANANTHAPURAM-695017

HLL/AFT/PUR/CHIMNEY-BOILER/2013-2014	19/02/2014

### TECHNICAL SPECIFICATION & GENERAL CONDITIONS

The scope of the work includes the following.

- Fabrication, Supply, Erection and Installation of Self supported Chimney of Forbes Marshal make 2 Ton Boiler as per drawing and conforming to the requirements of is code of practice is 6533 part1, 1989,(reaffirmed 1998) and is 6533 part2 1989.

- Provide protective coatings at heatends, Painting Chimney as per is code of practice is 6533   part1.

- Provide necessary stay wire with proper footings as stipulated in the code of practice is 6533, if necessary.

- Provide necessary earthing, lightening arrester and aviation lamp as per the drawing.

GENERAL CONDITIONS

- The work should be done in consultation with HLL   Engineers/Supervisors.

- All statutory deductions will be effected from bills as per the rules of the company.

- All safety precautions relating to the work on contract should be taken by you and in this respect, necessary safety permit should be obtained by the Contractor from the Engineering department of the company.

- All workers employed by the Contractor shall perform their duties under your own control and supervision.

- The workers engaged by the Contractor will be paid wages not less than the wages as per the statutory provision under the minimum wages act.

Schedule – A

Page 2 of 5

- The Contractor will be fully responsible for the acts or omission of the workers employed by you and shall indemnify and save the company from and against any such losses and expenses there by caused.

- Necessary insurance coverage shall be taken by the Contractor in respect of any injury or fatality of any person employed by you.

- The Contractor shall comply with all applicable law and orders, rules and regulations of the state Government of Kerala and Govt. Of India in respect of the work.

- The work should be carried out without causing any inconvenience to the factory work and shall ensure that no damage is occurred to the existing plant and machinery.

- The management reserves the right to accept or reject the tender either partially or fully without assigning any reason what so ever.

- All materials, consumables and any other items which is not mentioned (with regard to the work) will be under the scope of the Contractor.

- The Contractor has to obtain necessary sanction and approvals from statutory bodies like Kerala State Pollution Control Board, Inspectorate of Factories & Boilers and others if any before the commencement of work.

- Penalty will be deducted if the work is not completed in specified time.

- The party has to submit the offer given in SCHEDULE-F.

- Stability certificate is to be obtained from competent Authority and to be produced to the Officer-in-Charge of Engineering department along with commissioning of chimney.

- Stay wire support is to be provided to the chimney at 120 Degree.(if necessary).

- Provision for flue gas analysis is to be incorporated in the chimney as per standard.

- Necessary civil works shall be done by HLL, for which drawing contains necessary specification to be submitted by the Contractor after getting confirmed offer from HLL.

- Yessab/ Advani make Welding Rod shall be used for the Welding work.

- TATA/SAIL make MS Plate of 6,8,10 & 24 mm thickness  shall be used for fabricating chimney and as per IS 2062 code.

Schedule – A

Page 3 of 5

DRAWING:

Schedule – A

Page 4 of 5

CHIMNEY DESIGN

Location

Total Boiler Capacity                  2800        Kg/hr F&A 100º C

Total Fuel Consumption             170.1        kg/hr

S %                                              3.5

SO2                                             11.91        kg/hr

Calculated Height                        29.44       mtr

Exit gas volume                           4301.90   m³/hr

Flue gas temp at boiler outlet      250          deg C

Calculated diameter                    356.08      mm

Basic Wind Speed                       39.00        m/s

Risk Coefficient, K1                   1.00          Table 1, Cl. 5.3.1 - IS 875 Part 3 (for 50 year Life)

Topography factor, K3               1.00

Importance Factor                       1.50         Table 4, IS 1893 – 1984

Dimensions

Chimney Type                            Fully Welded

ID at Top                                     355          mm

Height of chimney                      30            m

Cone height                                 30            m

ID at base                                    1200        mm

Number of zones                         10

Corrosion allowance                   1.5           mm

Area of ladder                              0.3          m²/m

Weight of ladder                         30            kg/m

Wt of Helical strakes 50 x 3 thk,

3# at                                             5             kg/m

2.2575 mtr pitch on top straight

portion

Area of each platform                 1.5          m²

Terrain Category                         2

Terrain Class                              Class B

|  | Zone No | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Zone height | m | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 |
| Zone top height | M | 30.00 | 27.00 | 24.00 | 21.00 | 18.00 | 15.00 | 12.00 | 9.00 | 6.00 | 3.00 |
| Zone thickness | mm | 6.00 | 6.00 | 6.00 | 8.00 | 8.00 | 8.00 | 8.00 | 10.00 | 10.00 | 10.00 |
| Zone top ID | mm | 355.00 | 439.50 | 524.00 | 608.50 | 693.00 | 777.50 | 862.00 | 946.50 | 1031.00 | 1115.50 |
| Zone bottom ID | mm | 439.50 | 524.00 | 608.50 | 693.00 | 777.50 | 862.00 | 946.50 | 1031.00 | 1115.50 | 1200.00 |
| Platform Provided ? |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |
| Platform height from ground level | m | 28 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |
| Platform Angle |  | 360 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 |

Design wind pressure                               112.60    kg/m2

Allowable deflection due to wind load    150.00    mm

Schedule – A

Page 5 of 5

Actual deflection due to wind load          148.10    mm

Total design Bending Moment (Mk)        70,846    kg-m

Total design Shear Load                           2,452      Kg

Stress Calculations

| Condition for Buckling Stability ( Clause 7.7) | Safe | Safe | Safe | Safe | Safe | Safe | Safe | Safe | Safe | Safe |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Stability check for tensile stress (clause 9.1.1) | Safe | Safe | Safe | Safe | Safe | Safe | Safe | Safe | Safe | Safe |

Base Chair Design

Base Plate OD                                           1800       mm

Base ring width                                         350         mm

Skirt dia                                                    1200        mm

No. of bolts                                               20

PCD of bolts                                             1500        mm

Bolt size selected                                      32            mm

Bolt length reqd to be grouted in M20

concrete as per IS 456 -1978                    1068        mm                        (to be checked by client based on actual site conditions)

Min. Bolt length required.                        1820        mm

Bottom plate thickness                              48           mm

Top Base plate thickness provided           24           mm

thickness of vertical stiffener (2 / bolt)     10.00      mm

Flange Details (if Applicable) with Trapezoid gussets (100 x 125 x 8 thk) between flanges

|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Flange ID | mm |  |  |  |  |  |  |  |  |  |  |
| Flange OD | mm |  |  |  |  |  |  |  |  |  |  |
| Bolt PCD | mm |  |  |  |  |  |  |  |  |  |  |

No. of bolts

Bolt dia (selected)                               mm

Bolt length                                          mm

Flange Thickness (selected)                mm

Weights

Shell                                                    6,881 Kg

Base Chair                                          1,536 Kg

Misc                                                      480 Kg

Total                        8,900 Kg (This is approx wt, while preparing drawing exact weight needs to be calculated)

Schedule – B

Page 1 of 2

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

THIRUVANANTHAPURAM-695017

HLL/AFT/PUR/CHIMNEY-BOILER/2013-2014                   			19/02/2014

### III. QUESTIONNAIRE

(General information of the supplier)

1.	Name & Address of the supplier with			:

(a) Telephone No.

(b) Fax No.

(c) E – mail Address

(d) Name of the contact person

(e) Whether proprietory / partnership /

Limited company.

2.	Are you a manufacturer, authorized			:

Dealer or any other? If authorized agent,

A copy of the original letter from the

Manufacturer / Principal, duly attested,

Should be furnished conforming the agency

3.	How many years have you been in the 	            :

business of manufacturing

4.         What would be the minimum period			:

required to deliver the machine from the date of

confirmed Purchase 	order?

5.	Have you been a supplier / manufacturer,		:

if so details of the name, address,

quantity and values of orders

received and executed during

last three years? (Attach separate sheet)

Schedule – B

Page 2 of 2

6.	What is your Annual Turn Over during the 	         :

last 3 years?

7.	What is your :-				         :

a) CST No                                                               :

b) VAT NO /TIN NO                                              :

c) Central Excise Registration No:		         :

d) PAN No                                                              :

8.	Name & Address of your Banker(s)		         :

9.	Any other details				         :

All the information provided herein is true & correct.

PLACE:					NAME & SIGNATURE OF THE APPLICANT

DATE:					           		(WITH OFFICE SEAL)

***

Schedule – C

Page 1 of 3

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

THIRUVANANTHAPURAM-695017

HLL/AFT/PUR/CHIMNEY-BOILER/2013-2014                                                    19/02/2014

### IV. TERMS & CONDITIONS

1. The tender should be completed in all respects; incomplete tenders are liable to be rejected.

2. Unsealed tenders received are liable to be rejected and this will be at the sole risk of the tenderers.

3.Earnest Money deposit (EMD)

  - Technical Bid should accompany a DD drawn in favour of M/s.HLL Lifecare Limited, and payable at Thiruvananthapuram for a sum of Rs. 10,000/- (Rs. Ten Thousand only) towards Earnest Money Deposit  failing which the Tender is   likely to be summarily rejected.

  - Release of EMD: The EMD of unsuccessful tenderers will be refunded soon after finalisation of tender, or after two months from the date of opening of tender whichever is earlier. The EMD will not bear any interest.

  - Forefeiture of EMD: The EMD will be forfeited by the HLL in case, after submitting the tender, the tenderer withdraws his offer or fails to supply after the receipt of Purchase Order.

4. SUPPLY:

The successful tenderer will have to supply the machine   within the stipulated delivery time mentioned in the Purchase order.

5. PERIOD OF VALIDITY OF TENDER:

The tender will remain open for acceptance for 30 days from the date of opening of the tender and the rate quoted shall be firm and valid for a period of 90 days from the date of opening of the quotation.

6. TERMINATION OF CONTRACTS:

In case, after issue of a firm order, the successful tenderer fails to supply the item as per the specified quality and the required quantity according to the Delivery Schedule as given in the Supply Order, and even fails to complete the supply within the extended period if any given in writing by HLL Lifecare Limited, Thiruvananthapuram, it will be within HLL’s full rights to terminate the contract by giving a notice of 21 days in writing sent by Registered courier to the

Schedule – C

Page 2 of 3

address given in the tender submitted or to any other address which may be recorded in the office at the request of the tenderer. The period of 21 days will be counted from the date of issue of the notice.

In case of notice sent by registered post/ courier to the address recorded in the office as is returned undelivered with the remark addressee not found or addressee refused to accept, the notice shall be deemed to have been served and the termination will automatically take effect from the 22nd day of dispatch of the notice.

HLL Lifecare Limited, will have the full right to reject any or all the tenders without assigning any reason whatsoever. The HLL Lifecare Limited, also reserves the right to award the contract with more than one contractor.

7. PRICE:

Price: The tenderer has to quote the rate for supply of the item as per unit as given in the tender.  Statutory levies if any such as Excise   Duties, Sales Tax, VAT etc. should be shown separately.  Rates quoted should be strictly as per HLL’s format.

Price variation: Rate quoted shall be firm and valid for a period of one year from the date of opening of the tender.  The benefit of reduction of statutory levies should be passed on to the purchaser.

8. RELEASE OF PURCHASE ORDER:

The purchaser may consider placement of a purchase order for commercial supplies on those bidder(s), whose offers have been found technically, commercially and financially acceptable.

During the period of contract, if so desired by the purchaser, the supplier (s) premises shall be visited by the purchaser for inspection/evaluation.

9. PAYMENT:

A. Supply

- 60% of the order value against supply of all items.

- 30%  of order value against successful Commissioning

- 10% will be retained as Retention Money which shall be paid after one year from the date of successful SAT OR shall be paid against a performance bank guarantee for an amount equivalent to 10% of order value from a scheduled bank with validity of one year from date of successful Commissioning.

Normally the Purchaser will not entertain any advance payment. However, the bidder can indicate advance payment in the payment terms, if required. Moreover such advance payment, will be released against submission of a Bank guarantee, on a specific format given by the supplier, from a nationalized/scheduled bank for like amount valid up to the supply of equipment

at purchaser’s site.

Schedule – C

Page 3 of 3

B. Installation

- 100% of work order against successful SAT

10. Warranty: One year from the date of successful commissioning.

11. PURCHASER’S RIGHT TO ACCEPT ANY BID AND TO REJECT ANY OR ALL BIDS

The Purchaser reserves the right to accept or reject any bid, and to annul the bidding process and reject all bids, at any time prior to award of contract without assigning any reason whatsoever and without thereby incurring any liability to the affected bidder or bidders on the grounds of purchaser’s action.

12. TRAINING

The bidder shall provide necessary training for operation & maintenance staffs of the purchaser at free of cost.

13. Mode of Transport:

By road for Indian Suppliers unless otherwise specified.

14. Despatch documents like delivery note/challan, packing list and invoice should be intimated immediately with the LR No/Shipping Bill No/Air way Bill No.

15. The jurisdiction of any disputes, suits and proceedings arising out of this   tender shall be only in the courts of Thiruvananthapuram, Kerala State, India.

16. “Any disputes or difference whatsoever arising between the parties out of or relating to the construction, meaning and operation or effect of this contract or the breach thereof shall be settled by arbitration in accordance with the rules of arbitration of the Indian Council of Arbitration and the award made in pursuance thereof shall be binding on the parties” in case the matter is referred for arbitration.

17. The decision of HLL will be final and no correspondence on this shall be entertained.

18. There will not be any post tender negotiation except with the first lowest responsive bidder.

19. The jurisdiction of any disputes, suits and proceedings arising out of this   tender shall be only in the courts of Thiruvananthapuram, Kerala State, India.

20. The decision of HLL will be final and no correspondence on this shall be entertained.

JGM (Materials)

SCHEDULE – D

Page 1 of 1

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

THIRUVANANTHAPURAM-695017

HLL/AFT/PUR/CHIMNEY-BOILER/2013-2014                				19/02/2014

V. INDEMINITY CLAUSE:

If the supplier fails to execute the order within the time prescribed for the delivery of goods ordered or violates or infringes the existing rates as agreed to as mentioned in the supply order, the supplier shall and will indemnify the company against all loses or damages whatsoever to be incurred or sustained including the legal cost or expenses incurred by the company by reason of non-delivery of equipment at agreed quantity and rate with in the time specified in the supply order.  The company will initiate legal action if the supplier fails to execute the supply order as per the schedule in the supply order for the actual loss suffered. Responsiveness of the Bid shall be at the discretion of HLL.

The supplier shall have no right to change the conditions stipulated in the supply order.

Bid pronounced Non Responsive by HLL shall be summarily rejected.

The decision of HLL will be final and no correspondence of this shall be entertained.

We have read and understood the above conditions and agree to abide   by the same.

PLACE:                                    NAME AND SIGNATURE OF THE APPLICANT

DATE:                                                          (WITH OFFICE SEAL)

***

SCHEDULE - E

Page 1 of 1

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

THIRUVANANTHAPURAM-695017

HLL/AFT/PUR/CHIMNEY-BOILER/2013-2014          				19/02/2014

VI. DECLARATION

We confirm having read and understood all the specifications, instructions, forms, terms and conditions and other requirements of the above tender (both expressed and implied) in full and that we agree to abide by all without any deviation.

SEAL OF THE APPLICANT		                         	                  SIGNATURE

NAME AND ADDRESS OF APPLICANT

***

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

# THIRUVANANTHAPURAM-695017

Email: materialsaft@lifecarehll.com

Website: www.lifecarehll.com

PH:  +91 471 2442641, 2445930

FAX: +91 471 2445935

### INVITATION FOR BID

(PRICE BID)

# FOR

FABRICATION, SUPPLY, ERECTION AND INSTALLATION OF

SELF SUPPORTED CHIMNEY FOR FORBES MARSHAL MAKE 2 TON BOILER

Quantity: 1 Number

AT

AKKULAM FACTORY

THIRUVANANTHAPURAM – 695 017

SCHEDULE - F

Page 1 of 2

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O,

THIRUVANANTHAPURAM-695017

VII. PRICE BID

NAME OF THE ITEM: FABRICATION, SUPPLY, ERECTION AND INSTALLATION OF

SELF SUPPORTED CHIMNEY FOR FORBES MARSHAL MAKE 2 TON BOILER

| Sl. No: | Particulars | Unit | Qty | Rate (Rs.) | Amount (Rs.) |
| --- | --- | --- | --- | --- | --- |
| 1. | Fabrication, Supply, Erection and Installation of Self supported Chimney of Forbes Marshal make 2 Ton Boiler as per drawing and conforming to the requirements of is code of practice is 6533 part1, 1989,(reaffirmed 1998) and is 6533 part2 1989. | No | 1 |  |  |
| 2. | Provide protective coatings at heatends, Painting Chimney as per is code of practice is 6533 part1, | Ls |  |  |  |
| 3. | Provide necessary stay wire with proper footings as stipulated in the is code of practice is 6533, if necessary. | No | 3 |  |  |
| 4 | Provide necessary earthing, lightening arrester and aviation lamp as per the drawing | No | 1 |  |  |
| Total Amount (Rs.) |  |  |  |  |  |
| Excise Duty |  |  |  |  |  |
| Sales Tax |  |  |  |  |  |
| Other charges (if any) |  |  |  |  |  |
| Service Tax |  |  |  |  |  |
| Grand Total (Rs.) |  |  |  |  |  |

SCHEDULE - F

Page 2 of 2

Statutory levies if any	:

Any other Remark (s)	:

Payment terms:

Certified that the rate quoted will hold good for 90 days, during which period no upward revision will be asked for.

NAME OF TENDERER: ______________________________

Place:                                 ADDRESS AND SIGNATURE OF THE TENDERER                                                           Date:                                                                                    (WITH OFFICE SEAL)