HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O.,

# THIRUVANANTHAPURAM-695017

Email: materialsaft@lifecarehll.com

Website: www.lifecarehll.com

PH:  +91 471 2445930, 2442641

FAX: +91 471 2445935

TECHNICAL BID

TENDER FOR

ANNUAL MAINTENANCE CUM RUNNING CONTRACT FOR A/C PLANT

HLL/AFT/PUR/ENGG/AC-RUNNING/2013-2014                      24/04/2013

TENDER NOTICE

Dear Sir,

Sub: Annual maintenance cum running contract for A/C plant  reg:-

Sealed and super scribed tenders are invited under two bids system (Technical & Price) in the prescribed form Authorized Agent (s) / Competent venders for Annual maintenance cum running contract for A/C plant to our AKKULAM Factory, Thiruvananthapuram for the year 2013-14

The detailed tender notice & documents can be downloaded from our website www.lifecarehll.com. Amendments if any to this tender notice will be published only in our website.

The completed tenders must reach to the JGM (Materials), HLL Lifecare Limited, Sreekariam - P.O, Trivandrum, Pin- 695017, Kerala, on or before 2 pm on 15/05/2013 and it shall be opened at 3.00 pm on the same day.

The tender no. & date of opening must invariably be mentioned at the top of the cover.

JGM (Materials)

Ph No: +91 471 2445930

Fax No: +91 471 2445935

Email: materialsaft@lifecarehll.com

## HLL LIFECARE LIMITED

Akkulam Factory

THIRUVANANTHAPURAM-695017

###### CONTENTS OF BIDDING DOCUMENTS

| Sl No | Schedule | Description | Page No |
| --- | --- | --- | --- |
| TECHNICAL BID |  |  |  |
| 1. | Schedule – A | General Terms & Conditions | 4 – 8 |
| 2. | Schedule – B | Details of A/C Unit | 9 |
| 3. | Schedule – C | Contract Details | 10-11 |
| 4. | Schedule – D | Special Conditions | 12-13 |
| 5. | Schedule – E | Work Details | 14 |
| PRICE BID |  |  |  |
| 1. | Schedule – F | Price Bid Form | 16 |

Schedule - A                                                                                                                           Page 1 of 5

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O.,

# THIRUVANANTHAPURAM-695017

###### General Terms & Conditions

- Sealed and superscribed tenders are invited for the Annual maintenance cum running contract for A/C plant at HLL Lifecare Limited, for a period of One Year as per the terms and conditions as format given below.

| Tender No: | Date of opening of Technical Bid |
| --- | --- |
| HLL/AFT/PUR/ENGG/AC-RUNNING/2013-2014 | 15/05/2013 at 3.00 PM |

- A complete set of bid documents can be had from the office of the JGM (Materials), HLL LIFECARE LTD, AKKULAM, THIRUVANANTHAPURAM-695 017 during office hours on any working day on submission written application and remitting a non-refundable fee of Rs. 520/- (including taxes) by cash or in the form of DD drawn in favour of HLL Lifecare Limited, Akkulam, Thiruvananthapuram.

The Tender Documents can also be down loaded from our Website www.lifecarehll.com and cost of the Tender Documents as mentioned above should be furnished along with Technical Bid.

Re-word- processed formats or tenderers own formats for the technical bid/ price bid will disqualify the tender.  Tender forms shall be filled in ink or typed.  No tender filled in pencil shall be considered.  The tenderer shall sign and seal the form at each page and at the end, in token of acceptance of all the terms and conditions of the tender.

Tender Bids received without the cost of Tender Documents shall be summarily rejected.

Schedule - A

Page 2 of 5

The bid documents will be available up to 15.00 Hrs on the previous working day of the opening of Technical Bids.

- Tenders in prescribed form should be submitted in sealed covers and super scribed “Tender for Annual maintenance cum running contract for A/C plant” and sent to JGM (Materials), HLL Lifecare Ltd, Akkulam Plant, Sreekariyam P.O., Thiruvananthapuram, Kerala, India so as to reach here before 14.00 hrs on 15/05/2013 by registered post/courier acknowledgement due or should be deposited in the tender box available in this office. No acknowledgement will be made separately. The undersigned will not be responsible for any tender handed over to any official of this office in person. Tenders will be opened at 15.00 hrs on 15/05/2013 in the presence of the tenderers or their authorized agents who may choose to be present.

- Earnest Money Deposit: Each tender should contain an Earnest Money Deposit of Rs. 10,000/- (Rupees Ten thousand only). This amount can be remitted by Demand Draft drawn in favour of the HLL Lifecare Ltd, obtained from any scheduled bank and payable at Trivandrum. The Demand Draft towards EMD should be attached along with the tender. Tenders without proper EMD will be rejected outright.

- Release of EMD: The EMD of unsuccessful tenderers will be refunded soon after finalization of tender, or after two months from the date of opening of tender which ever is earlier.  The EMD will not bear any interest.

- Forfeiture of EMD: The EMD will be forfeited to the HLL in case, after submitting the tender, the tenderer withdraws his offer or fails to execute the agreement when called for to do so.

- Security Deposit: The successful tenderer will have to remit an amount of Rs. 20000 (Rupees Twenty Thousand only) as Security Deposit.  This amount can be remitted by Demand Draft drawn in favour of HLL Lifecare Limited payable at Trivandrum.  The EMD of the successful tenderer will be adjusted against the Security Deposit.

Schedule - A

Page 3 of 5

- Agreement: The successful tenderer will have to execute an agreement after remitting the Security Deposit in Stamp Paper for Rs.100/. at his expenses within 7 days of issue of the letter.

- The HLL will have the full right to reject any or all the tenders without assigning any reason whatsoever and is not bound to accept the lowest tender. The HLL also reserves the right to award the contract with more than one contractor.

- If the last date fixed for receipt of tender for opening, ie, 15/05/2013 is declared a closed holiday, the tenders will be received on the next working day up to 14.00 Hrs and opened at 15.00 Hrs on the same day.

- HLL shall not be responsible if the bids are delivered elsewhere.

- Bid Opening:

- The bids shall be opened on date and time as specified, in the presence of such bidder(s) or their representatives who may be present.  The bidder(s) or the authorized representative(s) who are present shall sign an attendance register.  The authorized representative(s) of the bidder(s) shall submit letter(s) of authority before they are allowed to sign the attendance register and participate in the bid opening.

- The Technical Bid will be opened on the prescribed tender opening date and time.  The price bid will be opened on a later date, which will be made known to all eligible bidders, after technical evaluation has been completed.

- The bids which are found as substantially responsive in the technical evaluation and comply with all the requirement, shall only be considered for financial bid opening.   The financial bid (price schedule) submitted by such tenderers whose technical bid have been considered as technically unacceptable on the basis of evaluation, will not be opened.

- The decision of HLL will be final and no correspondence on this shall be entertained.

##### Schedule - A

##### Page 4 of 5

- The Price Bid must be submitted strictly as per format given by HLL.

14. Bid Validity

  - The validity for the bid shall be 3 months.

  - There will not be any price escalation during the agreement period of one year.

- The Price Bid of those Tenderers who qualify in the Technical Bid only will be opened.  Those bidders whose qualified in the bid but not an approved vendor in Akkulam Factory (AFT) their price bid will be opened only when they become an approved vendor after successful completion of vendor development protocol. The Price Bids of Tenderers who do not qualify will be returned unopened. The date and time of opening of price bid will be intimated separately.

- Those bidders who download the tender documents from our website should furnish the Name and address of the vendor, name of contact person, telephone & Fax numbers and Email details immediately by fax/Email.

- Any changes pertains to this tender shall be communicated only through our website www.lifecarehll.com

- (i): Termination of Contracts: In case, after issue of a firm work order, the successful tenderer fails to execute the work as per the specified quality and the required quantity according to the Delivery Schedule as given in the Work Order, and even fails to complete the supply within the extended period if any given in writing by HLL,  Trivandrum, will be within HLL’s full rights to terminate the contract by giving a notice of 21 days in writing sent by Registered courier to the address given in the tender submitted or to any other address which may be recorded in the office at the request of the tenderer. The period of 21 days will be counted from the date of issue of the notice.

(ii). HLL, Trivandrum reserves the right to terminate the contract without assigning  any reason by giving a notice of 21 days to the successful tenderer by Regd Post to the address given in the tender submitted, or to any other address which may be recorded in the office at the request of

##### Schedule - A

Page 5 of 5

the tenderer. The period of 21 days will be counted from the date of dispatch of the notice. In such cases, the Security Deposit of the successful tenderer will be refunded soon on getting demand from the tenderer. The HLL will not be liable for payment of any compensation for any loss that the contractor may be put to or alleged to have been put to on account of such termination.

- In case of notice sent by registered post/ courier to the address recorded in the office as per clause 25(i) & (ii) is returned undelivered with the remark addressee not found or addressee refused to accept, the notice shall be deemed to have been served and the termination will automatically take effect from the 22nd day of dispatch of the notice.

- HLL will have the full right to reject any or all the tenders without assigning any reason whatsoever. The HLL also reserves the right to award the contract with more than one contractor.

- The tender should be submitted on OUTER ENVELOPE SEALED AND SUPERSCRIBED “DO NOT OPEN BEFORE 15.00 HRS ON 15/05/2013 addressed to this Office containing the following TWO INNER SEALED ENVELOPE.

  - Cover contains Acceptance of Terms &Conditions, Technical Bids and EMD (should be superscribed)

  - Cover contains Price Bid (should be superscribed)

For and on behalf of the HLL

JGM (Materials)

For HLL, AFT, Trivandrum-695 001

We have read and understood the above conditions and agree to abide by the same.

PLACE:                         NAME AND SIGNATURE OF THE APPLICANT

DATE:                                                                  (WITH OFFICE SEAL)

Schedule - B

Page 1 of 1

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O.,

# THIRUVANANTHAPURAM-695017

## ANNEXURE-I

| ### DETAILS OF A/C UNITS |  |  |  |
| --- | --- | --- | --- |
| Sl No: | ITEMS | CAPACITY | QTY IN NO: |
| 1. | Blue star Chiller | ##### 145TR | 2 |
| 2. | Batliboi AC Plant | 40T | 2 |
| 3. | Split AC Units | .8T to 1.5T | 10 |
| 4. | Split AC 2T |  | 1 |
| 5. | Chiller Unit (Package Unit) | 2T | 1 |
| 6. | Refrigerators |  | 5 |
| 7. | Refrigerated Air Drier |  | 2 |
| 8. | Incubator |  | 3 |
| 9. | Refrigerator Water Bath |  | 1 |
| 10. | Refrigerated Centrifuge |  | 2 |
| 11. | Fan Coil Units | 2T | 10 |
| 12. | AC Package Plant (IT) | 8T | 1 |
| 13. | AC Package Unit (IT Lab) | 5T | 2 |
| 14. | Chiller Unit | 3T | 4 |

Schedule - C

Page 1 of 2

## ANNEXURE-II

### MAINTENANCE CONTRACT OF AIR CONDITIONING SYSTEM

- To attend any break down or defects in (Mechanical/Electrical) plant as and when called for.

- To carry out repair and resetting of all equipment in the plant as and when required, for efficient functioning of the plant.

- To carry out monthly preventive maintenance as specified below.

  - Checking of all equipment and controls in the plant & rectification or defects if noticed any.

  - Cleaning of cooling Towers.

- To carry out quarterly preventive maintenance as listed below.

  - Checking and rectification of inter-locking arrangements of complete system of HP, LP, OP cut outs thermostats, water pressure switches in condenser water lines, pressure switches in chilled water lines, inter locking of compressor with condenser water pumps, chilled water pumps, cooling tower motors etc.

  - Checking of main control panel, AHU electrical panel, checking of starters, lower loads, single phase prevent or cleaning of starter contracts and connections.

  - Descaling of water pipe lines inter connecting condensers, condensers pumps and cooling tower nozzles, by circulating Mac solution in the systems.

Schedule - C

Page 2 of 2

  - Descaling of water tubes of horizontal shell and the Tube condenser with chemical solution and cleaning of condenser tubes with nylon brushes and replacement of condenser head gas-kets.

  - Checking of loading/unloading mechanism of refrigeration compressor to ensure proper functioning.

  - Check cooling coil fins for dirt accumulation.  Clean if found necessary.

  - Checking and tightening of electrical connection and contacts.

  - Reconditioning of cooling tower fan.

  - Inspection of foundation bolts.

  - Changing of compressor oil after proper sample analysis.

  - Any other work related with A/C system, which arise from time to time.

To carry out yearly preventive maintenance as listed below.

- Overhauling of refrigeration compressors and changing of compressor oil.

- Reconditioning of condensor water pumps and changing of Bearings and gland packing if required.

- Reconditioning of chilled water pumps and changing of Bearings and gland packing if required.

- Balancing of blowers (AHU’s)

- Monitoring Hepa filter performance and replacement.

- Maintenance of pipes, ducts, duffusers grills etc.

- Vibration monitoring if found necessary.

- Painting of water lines and frames.

- Fabrication of supports/frames if necessary.

- Any other works related with A/C Systems, which arise from time to time.

- Re conditioning of cooling towers.

Schedule - D

Page 1 of 2

ANNEXURE – III

# SPECIAL CONDITIONS

1.Every month or as and when required one qualified senior and experienced Engineer from the contractor’s side shall visit HLL Lifecare limited AFT A/C plant and conduct necessary inspection and preventive maintenances.   Record should be submitted to DGM (Engg).

2.Two experienced skilled operator’s/shift at any time shall be available for running the A/C plant and one qualified supervisor personnel with min.5 years experience in the relevant field shall be available in the General shift.  The contractor shall keep the plant running without any shut down.

3.Contract should have adequate workshop facility in Trivandrum for carrying out all maintenance work of A/C system.

4.Contract includes all kinds of maintenance work related to AC plant, AHU, Cooling Tower etc in the system comprising all Mechanical, Electrical and instrumentation works. Including breakdown maintenance work. Breakdown work shall be attended in minimum possible time (If required additional labour is to be deputed and prepared to work round the clock)

5.The contractor should have 5 years experience in maintenance and operation of any centralized A/C plant of   capacity 40 TR and above.

6.The employees for the operation and maintenance should have S.S.L.C with ITI certificate in Refrigeration and Air conditioning and should have at least 2 years experience in operation and maintenance of such centralized plants.

Schedule - D

Page 2 of 2

7.For every instance of negligence resulting in production loss, 25 % of the monthly bill will be deducted from the contract amount.

8.In case of installation of any additional A/C plant, during the contract period, the contractor has to operate the same and do the necessary maintenance without any additional charge.

9.All the tools required for the work has to be brought by the contractor.  A set of necessary tools should be kept in the plant for daily use.

10.The contractor shall ensure that his workmen is getting the minimum wage for operation and maintenance of A/C plant as per the minimum wages applicable for minor engineering works.

11.All the statutory deductions like Income tax, PF, Work contract tax, etc if applicable shall be deducted from each bill.  The details of the persons engaged by the contractor their name, designation and the salary drawn by them must be furnished along with every claim.

12.A security deposit to the extend of 10 % of the total value of contract should be deposited immediately after receipt and acceptance of work order.

13.All spares and consumables required will be supplied by HLL.  If any spares are not available with HLL the same shall be arranged by the contractor.  The amount of such spares shall be made by HLL on actual basis.

Schedule - E

Page 1 of 1

#### ANNEXURE-IV

#### A/C Operation Contract is inclusive of the following

- Cleaning air filters

- Cleaning water strainers

- Check AHU drive set and tightening if required

- Checking leakage of refrigerant

- Lubricating the bearings

- Checking and tightening of electrical connections and contacts.

- Checking regular plant performance.

- Inspection of controls for proper operations.

- Cleaning cooling tower

10.Indicator lamp replacement

11.Fuse replacement

12.Maintaining logbook

13.Checking and tightening glands of pumps

14.Check spray of cooling towers

15.Checking compressor coupling for tightness

16.Clean drains wherever necessary

17.Vibration monitoring

25.Ensure the air changes, Temperature and humidity as per the Specifications.

19.Any other work related with A/C system, which arise from time       to time.

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O.,

# THIRUVANANTHAPURAM-695017

Email: materialsaft@lifecarehll.com

Website: www.lifecarehll.com

PH:  +91 471 2445930, 2442641

FAX: +91 471 2445935

PRICE BID

TENDER FOR

ANNUAL MAINTENANCE CUM RUNNING CONTRACT FOR A/C PLANT

##### Schedule - F

Page 1 of 1

HLL LIFECARE LIMITED

(A Government of India Enterprise)

AKKULAM PLANT, SREEKARIYAM P.O.,

# THIRUVANANTHAPURAM-695017

### PRICE BID

Price quoted as per the format given below.

| Description | Rate/Month (Rs) |
| --- | --- |
| Annual maintenance cum running contract for A/C plant |  |
| Total Amount (Rs.) |  |

Rupees -------------------------------------------------------------------- (in words)

Terms and Conditions:

- Rate shall be valid for a period of one year from the date of opening (for the financial year 2013-14)

- Price Bid strictly as per this format.

3. Statuary levies if any:

4. Other(s) Remarks if any:

Place:                       	                       Name & Signature of Applicant

Date:         							(With Office Seal)