TENDER

FOR

FIRE PROTECTION SYSTEM FOR NEW CANTEEN CUM STORAGE BUILDING,HLL, AKKULAM

PART-III

PRICE BID

TENDER NO. HLL/ID / 13 /49

JUNE 2013

HLL LIFECARE LIMITED

INFRASRTUCTURE DEVELOPMENT DIVISION

CONTENTS

| S.NO | ITEM | PAGE NO. |
| --- | --- | --- |
| 1. 2. 3. 4. 5. | Commercial Conditions Special Conditions Technical Specifications List of Approved makes of Material Bill of Quantities | 2-4 5-8 9-41 42 43 |

- COMMERCIAL CONDITIONS

    - The tendered rate shall inter alia be deemed to include for the provision of all materials, process, operation and special requirements detailed in the particular specification irrespective of whether these are mentioned in the description of equipment schedule and Bill of quantities or not. It is an express condition of the contract that the tendered rates for various items in the Bill of Quantities shall be deemed to include for the full, entire and final condition of the contractor respective items of the works in accordance with the provision of the contract.

    - The tendered rate shall include for all taxes, duties, etc. as applicable and shall be quoted on the works contract basis for Fire Protection system at New Canteen Cum Storage Building,HLL,Akkulam

    - The tendered rate shall remain firm and free from variation due to rise in the cost of materials/equipment, labour or any other reasons whatsoever during the contract period and valid extension on the case may be.

    - The quantum of excise duty included in the tendered price, the rate at which they were assumed etc. shall be indicated in the tender.

1.1	UNIT RATES

1.1.1. The tenderer shall indicate unit rates for items like piping, fixing valves etc as shown in the schedule.

1.1.2 Only approved work will be measured on completion and priced as per rates quoted           against the respective items.

1.2	BRIEF DESCRIPTION OF PRICING

1.2.1	Unforeseen difficulties for which provision has not been made in the tender will in no way relieve the successful tenderer from the full execution of the work.

    - The price quoted shall be the final amount for this finished work.

  - INCOME TAX

Any payment to the contractor as per contract, will be made after deducting income tax as per the rules and regulations.

  - SALES TAX AND EXCISE DUTY

The tenderer shall clearly indicate sales tax, Excise and other duties as applicable in his offer for carrying out this work. ANY BID STATING THAT THE TAXES ARE EXTRA WILL BE SUMMARILY REJECTED

1.5.    SUBMISSION OF BILL

1.5.1.	The contractor shall from time to time prepare and submit interim bills of the work executed and on completion of the contract, he shall prepare and submit the final bill. The measurements sheets in support of the interim and final bills shall be prepared by the contractor on the basis of measurements taken by him jointly with the project engineer and the said measurement sheets shall be submitted by him with the relevant bill.

1.5.2.	Within the above frame work of the terms of payment the contract’s interim bills will have to be of a minimum value of Rs.5 lakhs only.

1.6.    EXTRA ITEMS

The contractor is bound to carry out any items of work necessary for the completion of the job even though such items may not have been included in the schedule of probable quantities or rates, such items being necessary or essential for completing the job. Variation order in respect of such additional items and their quantities will be issued in writing by the employer.

    - All shavings, cuttings and other rubbish as it accumulates from time to time during the progress of work and on completion including that of the sub-contractors and special tradesman and all materials condemned by the project engineer shall be cleared and removed from the site by the contractor without any extra charge.

    - All measuring steel taps, scaffolding, ladders instruments and tools that may be required for taking measurements shall be supplied by the contractor.

- 1.8.   OVER TIME WORK

If the contractor is required to work night or on holidays in order to maintain the time schedule, he shall take prior approval from the Engineer-in-charge. He should also provide and maintain at his own cost sufficient lights as may be necessary to enable the work to proceed satisfactorily during the night.

1.8.1. The contractor shall give full facilities to all other contractors working on site. He   shall also arrange his programme of work so as not hinder the progress of other trades. The decision of the Engineer-in-charge on any point of dispute between the various parties shall be final and binding.

- 1.8.2. It is specifically pointed out that the contractor shall not be entitled to any compensation whatsoever on account of delay in procurement or supply of controlled materials and the rates quoted in the contract are fixed till the completion of the contract.

- 1.8.3. The contractor shall co-operate with other agencies appointed by the owners for the work to proceed smoothly with the least possible delay and to the satisfaction of the owners, architects and the consultants.

- 1.8.4. The owners shall provide a source for power supply at one convenient point at site. The contractor shall at his own cost install a separate meter at the said source and lay additional cables from the said source also at his own cost. For the electricity consumed by the contractor he shall pay the owner the actual cost at the rate charged by the local authority for power for constructional purposes. The contractor shall also obtain the necessary permit for utilizing power for constructional purposes.

- 1.9     TERMS OF PAYMENT

- For equipments delivered and sorted at the site for the installation, the payment will be made by the HLL in accordance of this contract.

  - 75% of the contract value on pro-rata basis against open delivery of material at site and stored as directed by the HLL and after verification.

  - 20% of the contract value on satisfactory installation, testing and commissioning of the complete system/plant on pro-rate basis.

  - 5% of the contract value within one month of taking over.

  - Security Deposit: Security deposit will be deducted, a sum at the rate of 10% of gross amount of each running bill till the sum along-with the sum already deposited as earnest money, will amount to security deposit of 5% of the tendered value of the work. The Security Deposit will be released after the expiry of guarantee/ defect liability period or against submission of bank guarantee for an equivalent amount.

- SPECIAL CONDITIONS

2.1.    EXECUTION WORK

2.1.1.	The whole of the work as described in the contract (including bills of materials, specification and all drawings pertaining thereto) and as advised by the Engineer-in-charge from time is to be carried out and completed in all parts to the entire satisfaction of the Employer. Any minor details of construction which are obviously and fairly intended, or which may not have been definitely referred to in this contract, but which are usual construction practice and essential to the work, shall be included in this contact.

2.2.	CERTIFICATE OF COMPLETION

2.2.1	The contractor shall intimate to the Engineer-in-charge in writing as and when the works are completed and put into beneficial use in order to enable the consultants to check certify to the owners to take over the plants.

2.2.2	The work shall not be considered as completed and put into beneficial use until the consultants have certified in writing that the same has been completed and put into beneficial use.

2.2.3	The defects liability period of one year shall commence from date of such completion or any specific date mentioned therein.

2.3     Scope of Work

The Scope of work covers Fire Protection System at New Canteen cum Storage Building, HLL at Akkulam in accordance with drawings and specifications prepared under the direction and to the satisfaction of the HLL Lifecare Ltd.

2.4	Codes, Rules & Regulations

The firefighting installation shall be carried out in conformity to amendment no.3 to national building code of India (SP 7: 1983 part IV recommendation of TAC and the relevant BIS indicated in the various sections.

2.5 	Ascertaining Scope of Work

Intending tenderers are advised to study all the drawings, specifications, conditions etc. in details and inspect the site before submitting tenders so as to ascertain the nature and scope of the work involved and the method to be adopted in executing the work.

2.7	Inclusions in Rate

Rate quoted shall include cost of cutting holes and chase in walls, floor slabs, repairing the same and restoration of original surface wherever necessary, and cost of scaffolding if any. Nothing extra shall be entertained on this account. Any damage to walls, floors, etc. during installation and erection must be repaired by the contractor to match the original surface for which no extra amount will be paid.

2.8 	Material

All material, fittings and appliances used in the firefighting installation shall be new and of the best quality obtainable and of approved manufacturer and shall conform to the latest Indian Standard Specifications wherever they exist. Where Indian Standard Specifications are not available relevant British Standards shall become applicable. The tenderer shall indicate the make of various items of materials, which he proposes to use for their work. For the purpose a list of make of materials acceptable to the HLL is enclosed. The tenderer shall select any one out of these makes only. The Contractor shall replace the unapproved materials and fittings at his own cost.

2.9      Workmanship

Good workmanship and neat appearance are the pre-requisites for compliance with the various sections of these Specifications. The Work shall be carried out under direct supervision of a full time person holding certificate of competency issued by the State Government and in accordance with the statutory rules and regulations in force. The relevant I.S.I. code of practice shall be followed wherever applicable.

  - Drawings

The Electrical drawings indicate only the general scheme but not the exact routes of surface conduits/existing concealed conduits, exact position of switch boards, points, distribution boards etc., The Contractor shall prepare working drawings and have them approved by the Consultant before commencement of the work and the work shall be carried out as directed at site to the complete satisfaction of the Consultant.

2.11    Completion Drawings & Certificate

On completion of the work, completion drawings shall be prepared by the Contractor and two copies of the same submitted to the owner. In addition 2 soft copies in floppies/CDs in Auto CAD to be submitted.  The completion drawing shall indicate the following.  The rate quoted shall be inclusive of the same.

- The pump room layout.

- The control panel and wiring diagrams

- Sizes and routing of external fire hydrant piping

- Location of external and internal hydrants

- Location of wet risers and their sizes.

- Any other drawing as directed by the client/ Consultant.

2.12 SAFETY CODE

        - In respect of all labour employed directly or indirectly on the work for the performance of the fire fighting contractor’s part of work, the contractor at his own expense, will arrange for the safety provisions as per the statutory provisions, BIS recommendations, factory act, workman’s compensation act, CPWD code and instructions issued from time to time. Failure to provide such safety requirements would make the tenderer liable for penalty for Rs. 200/- for each violation. In addition the Engineer –in- charge shall be at liberty to make arrangements and provide facilities as aforesaid and recover the cost incurred thereon from the contractor.

        - The contractor shall provide necessary barriers, warning signals and other safety measures while laying pipelines, cables etc. or wherever necessary so as to avoid accident. He shall also indemnify CPWD against claims for compensation arising out of negligence in this respect. Contractor shall be liable, in accordance with the Indian law and regulations for any accident occurring due to any cause. The department shall not be responsible for any accident occurred or damage incurred or claims arising there from during the execution of work. The contractor shall also provide all insurance including third party insurance as may be necessary to cover the risk. No extra payment would be made to the contractor due to the above provisions thereof.

2.13 OTHER CONDITIONS

- Along with the tender document, the contractor should confirm the list of approved make of materials specified in the Tender which they are going to use.

- On award of work, the contractor should make the shop drawings and BOQ as per the site conditions and should be got approved from Client/ consultant before commencing the works.

- The entire factory made equipments shall be purchased and delivered to the site only after getting material approval from the technical officials of Client /consultant.

- The contractor has to submit a bar chart for the proposed execution before starting the work. The client/Consultant shall introduce necessary correction to it after discussion with the contractor.

- The materials are in accordance with the specification for permanent works.

- The materials are properly stored and protected against loss or damage or deterioration, to the satisfaction of the client/consultant.

- The contractor keeps a record of requirements, orders, receipt and consumption of materials in proper form and produces to the consultant/client for inspection. Ownership of such materials shall be deemed to vest in the client.

- The contractor should submit the list of workers and staff which they are going to deploy for the work along with contact details of project leader. The list should be got approved from client/consultant before commencing work. A technically qualified and experienced mechanical/ metallurgical engineer to be posted at site. He should be conversant with the modern practice of welding and modern fire fighting system.   He should be capable and competent enough to take decisions as and when required at site.

- Welding should only be carried out by a professional and experienced people who holds valued license issued by competent authorities like Cochin refineries, Gas authorities of India etc.  The true copy of the license is to be submitted to Client along with list of workers deployed for the work.

- Pipe sizes 50mm and below shall not be permitted to butt weld. Pipe sizes 50mm and below shall be socket welded with weldable socket fittings (drop forged) with rectifier welding machine.

- The contractor shall be instructed to strictly implement the welding process in line with the following standards: Code for Petroleum refinery piping Code of Practice for laying of welding pipes, Code for procedure for manual metal arc welding of mild steel for structural work, Welder Qualification: ANSI B 31.3 : IS: 5822, : IS: 823, ASME-SEC A IC. All codes referred shall be the latest editions.

- The contractor shall bear the cost of repair, changes replacement etc due to non-compliance with the standards, codes and this tender or due to disregard of the instructions given by the Engineer-in-charge.

TECHNICAL SPECIFICATIONS

FOR

FIRE FIGHTING SYSTEM

1.0    	TECHNICAL SPECIFICATIONS FOR FIRE FIGHTING SYSTEM

1.1    	General

Work under this subhead is time-bound and has to be completed within the time limit set in the tender. Work shall be executed in accordance with an agreed schedule which shall be submitted by the tenderers along with offer and agreed to by owners.

1.2  	Scope of Work

The scope of work in this subhead shall consist of furnishing all labour, materials, equipment and appliances necessary and required to completely do all work relating to the supply, installation, testing & commissioning of Fire Detection & Fighting System Works of HLL Lifecare Ltd, Akkulam Factory new canteen cum store building as described herein after and shown on the drawings. The scope of work in general shall include the following.

i)	External & Internal Fire Hydrant System.

ii)  	Sprinkler system.

iii)	Fire Detection System.

iv)	Hand Held appliances.

Without restricting to the generality of the foregoing, the work shall include the following:

A Hydrant System Covering the entire complex and consisting of the following:

A.   	Pumping system – To be tapped from the existing hydrant system of HLL Akkulam factory. The pumping system shall be properly checked and ensured that the system can achieve the necessary pressure.

B. 	Other piping system ancillaries such as Suction and Delivery Headers, Pressure Gauges, etc. as required.

C. 	External Hydrant Ring Main with single headed Yard Hydrants, RRL Hose, Branch Pipes, etc. all housed in a Hose Box.

D.	Internal Hydrant system where required with single headed landing valves accompanied by 1 number swinging type Hose Reel, 2 numbers RRL Hoses, Branch Pipe etc. all housed in the niche.  Bidder shall provide front frame with shutter for niche.

E.	Sprinkler system as indicated in the drawing.

F	Hand appliance as per Bill of Quantities.

G.	To obtain the approval of the relevant drawings before actual installation at site and to get the complete installation inspected and passed by the concerned authorities, as may be necessary as per local bye laws. (Any fee payable to the local bodies for such activities shall be reimbursed by the CLIENT/CONSULTANT on production of receipt).

1.3	Contractor’s Experience

1.3.1	Contractors shall engaged specialist agency only for this work of Fire Fighting systems.

1.3.2	The selected specialist agency must have sufficient experience in the execution of turn-key projects as specified.

1.3.3	Contractor must submit with the tender a list of similar jobs carried out by him as required along with the name of works, name and address of clients, year of execution, capacity of plant and value of work.

1.4	Technical Information

1.4.1	Contractor shall submit along with the tender copies of detailed specifications, cuts, leaflets, and other technical literature of equipment and accessories offered by him.

1.4.2	Contractor’s attention is specially invited to the special conditions and other clauses in the agreement which required the contractor to :-

a. 	Submit detailed shop drawings.

b. 	Use material of specific makes and brands.

c. 	Obtain all approvals from Fire Fighting authorities.

d. 	Execute the entire work on a turn-key basis so as to provide a totally operating plant.

1.5	Exclusions

1.5.1	Work under this contract does not include the following work:-

1.5.2	Electrical cables upto incoming motor control centre.

1.6	Site Accessibility

1.6.1	The equipments are to be located in pump house located within the Service block.

1.6.2	The equipment must be carried from the goods receiving station to the site in an extremely careful manner to prevent damage to the equipment building or existing services.

1.6.3	Contractor must visit the site and familiarize himself with above problems to ensure that the equipment offered by him are of dimensions that they can be carried and placed in position without any difficulty.

1.7	Approvals

The contractor shall prepare all submission drawings and obtain all approvals of fire fighting works from fire fighting authorities.

1.8	System Description

1.8.1  	The Hydrant System shall comprise of  AC  motor driven pump set, standby diesel pump  set, jockey pump (existing system) set for pressurization with   all  required  accessories  including  valves, special fittings, instrumentation, control panels and any other components required to complete the system in all respects.

1.8.2	The Hydrant System shall be semi automatic in action and shall be laid covering the entire area externally and all the floors internally with independent piping system. For the Sprinkler System, a separate piping system shall be installed.

1.8.3	The Hydrant System shall be kept pressurized at all times. The proposed Jockey Pump shall take care of the leakages in the system, pipe lines and valve glands.

1.8.4	The pressure in the hydrant pipe work shall be kept constant at 7 Kg/cm2.  In the event of fire when any of the hydrant valve in the network is opened, the resultant fall in header pressure shall start the AC motor driven fire pump through pressure switches automatically. There shall be one Diesel Engine Driven pump as standby for hydrant system.  In case of failure of electricity or  failure of Electric Pump to start on demand,  the  standby Diesel Pump shall automatically take over.

1.8.5  	However, shutting down of the pump set shall be manual except for the Jockey Pump which shall start and stop automatically through pressure switches. In addition to auto start arrangements, the main pump shall also have an over-riding manual starting facility by push button arrangement.

1.8.6	The piping for the hydrant system in the yard shall be laid in soil 1 Metre deep or in rectangular Trench. The pipe laid in soil shall be protected as specified in para 1.9.3 below. The scope of work includes necessary excavation of trench and back filling the same.  The scope of work also includes necessary watering, ramming, removing the surplus earth from the site and construction of brick pedestal at 3 Mtrs intervals of  size as indicated in the Bill of Quantities. Pipes shall be cleaned before wrapping and coating.

1.8.7	The yard hydrants shall be placed at a regular spacing of 30m - 45m centre to centre. The following accessories are proposed near each yard hydrant.

i)	One no. gunmetal single headed hydrant valves.

ii)	Two nos. RRL Hoses of size 63mm dia x 15m long.

iii)	One nos. gunmetal Branch pipe.

Gun metal hydrant valve, RRL hose and gunmetal branch pipe will be accommodated in an aluminium hose box mounted on brick pedestals.

1.8.8	The Internal Hydrant System shall be provided at points as indicated on the drawing on each floor.

1.8.9	The hydrant point shall be directly tapped from the Riser pipes, and shall be furnished with required accessories such as

i)	One no. gunmetal single headed hydrant valves.

ii)	Two nos. RRL Hoses of size 63mm dia x 15m long.

iii)	One no. first aid Dunlop hose reel full swinging type 20mm dia x 30m long.

iv)	One no. gunmetal Branch pipe.

The hydrant risers shall be terminated with air release valve at the highest points to release the trapped air in the pipe work. At each tapping from the Riser an Orifice Plate shall be located in the lower floors to reduce the pressure at no extra cost.

1.8.10	Sprinkler system shall be distributed so as to cover 10–12 sq. m area with one sprinkler.

Sprinkler risers shall be provided with instantaneous control valve with alarm gang. The alarm valve assembly shall be complete with all accessories as required for the performance.

A suitable drainage arrangement with bye pass valves shall be provided to facilitate maintenance of sprinkler pipe work.

1.8.11	To compensate for slight losses of pressure in the system and to provide an air cushion for counteracting pressure surges/water hammer in the underground pipe work Air Vessels shall be furnished in the pump room near fire pumps. The air vessel shall be normally partly full of water and the remaining being filled with air which shall be under compression when the system is in normal operation.

1.9	GENERAL SPECIFICATIONS

1.9.1	Pipes and Fittings

Pipes upto 150mm dia shall conform to IS-1239.  Pipes with dia 200mm and above (6mm thick) shall confirm to IS-3589.  All pipes shall be I.S.I. marked.  Fittings for black steel pipes shall be malleable iron suitable for welding or approved type cast iron fittings with tapered screwed threads.

1.9.2	Jointing

Joint for black steel pipes and fittings shall be metal-to-metal tapered thread or welded joints.  A small amount of red lead may be used for lubrication and rust prevention in threaded joints.

Joints between C.I. or black steel pipes, valves and other apparatus, pumps etc. shall be made with C.I. or M.S. flanges with appropriate number of bolts.  Flanged joints shall be made with 3mm thick insertion rubber gasket.

Note: Joints for pipes and fittings upto 50mm diameter shall be threaded joints using Teflon Tape or equivalent bonding tape on the threads.  Joints for pipe and fittings above 50mm diameter shall be welded joints.

1.9.3	Pipe Protection

- All pipes in under ground masonry trenches/service tunnels, above ground and in exposed locations shall be painted with one coat of red oxide primer and two or more coats of synthetic enamel paint of approved shade.

- Pipes in wall chases shall be protected from corrosion by 2 coats of bituminous paints.

- Protection of Underground Pipes:

The underground steel pipes shall be protected by coating and wrapping.  The coating and wrapping shall be done, in general, as per IS:10221-1982.

It specified in Bill of Quantities, the proprietary pipe protection system shall be provided as per the Manufacturers recommendation.  The proprietary system shall be of approved make.

1.9.4	Installation of Pipes

All pipes shall be adequately supported from ceiling or walls by structural clamps fabricated from M.S. structural e.g. rods, channels, angles and flats.  All clamps shall be painted with one coat of primer and two coats of black enamel paint.  The contractor shall provide inserts at the time of slab casting or provide suitable anchor fasteners.

The pipe supports or hangers shall be designed to withstand combined weight of pipe, pipes fittings, fluid in pipe and insulation.  Pipe supports shall be of steel and coated with rust preventing paint and finished with two coats black enamel paint.  The maximum spacing for pipes supports shall be as below:

Pipe (MM)			Spacing (MTR)		Size of support

Up to 25				2.0				6mm

32 to 65				2.4				8mm

75 to 125				2.7				10mm

150 & above				3.0				12mm

Pipes supports shall be spaced at maximum interval of 1.5 mtrs. on either side of heavy fitting and valves.  Wherever piping passes through walls, pipes sleeves of diameter larger than that of piping shall be provided.  Pipe sleeves shall be of steel or cast iron pipe.

The underground piping shall be supported with cement concrete blocks of suitable size and strength provided at an interval of 2.5 mtrs.  The pipes shall be laid at 1 mtr depth (top of the pipe) and trench excavated for sufficient width.  The rate for pipe shall include the scope of excavation/refilling the trench.  1:2:4 concrete thrust blocks are also to be provided at turning of pipe.  The cost of installation includes concrete pedestals etc. as required and to be included in the item rate.

1.9.5	Orifice Flanges

Contractor shall provide orifice flanges fabricated from 6mm thick stainless steel plates on the branch lines feeding different zones/floors so as to allow required flow of water at a pressure of 3.5 kg/sq.cm. for each hydrants and 2 bar at installation valve for sprinkler system.  The contractor shall design the orifices to ensure the required pressure. No extra cost shall be paid for the orifice plate.

1.9.6	Valves & Other Accessories

1.9.6.1	General

Each valve body shall be marked with cast or stamped lettering giving the following information’s:

a)	The manufacturer’s name or trade mark

b)	The size of the valve

c)	The guaranteed working pressure

Isolating valves on the water supply lines shall be full bore ball valve type for pipe diameters upto 50mm.  For 65mm dia and above these shall be butterfly valves.

1.9.7	Full Way Ball Valve

The valves shall be of full bore type and of quality approved by the Consultant/Owner.  The body and ball shall be of copper alloy and stem seat shall be of Teflon.

    - Sluice Valve (SV)

It shall be of IS 780  standards. Construction shall be of inside screw, non-rising stem for water purpose and flanged type.  Pressure class shall be of PN 1.0 and tested to 15 kG/Sq.cm pressure. Seat ring shall be of gun metal as per IS 318. Gasket packing shall be of CAF / Graphited asbestos.

1.9.9	Non-Return Valves

Non-return valves are to be IS:778-1984 manufactured from gun-metal or dezincification resistant brass.

1.9.10	Drain Valve

Drain Valves are to be provided at all low points in the system for draining the water.  These shall be 65mm dia full way ball valve fixed on 65mm dia pipe.

1.9.11	Inspection & Testing Assembly

Inspection and testing of the sprinkler system shall be done by providing an assembly consisting of gunmetal valves, gunmetal sight glass, bye-pass valve.

1.9.12	Flow Switch

Flow switch shall be provided on sectional mains and branch lines as indicated on drawings, or necessary and required and directed by the Engineer-in-charge.

Flow switch should be suitable to actuate at a minimum of flow and shall be suitable for connection to a central annunciation panel.

1.9.13	Pressure Switches

Pressure switches shall be differential type for operation of all pumps and for the various duties and settings required.  Pressure switches shall be for heavy duty operation and of approved make.  All pressure switches shall be factory calibrated.

1.10	External Fire Hydrants

Yard Hydrant valves shall be single headed as per IS : 5290.  The valve shall be complete with hand wheel, quick coupling connection spring loaded type and gun metal blank cap. The Yard Hydrant shall be laid on 125 and 100mm dia pipe as per standards. Hydrant Ring Main, branched off to 80 mm dia and Stand Post of 80mm dia.

1.11	Internal Landing Valves

The internal landing valves shall be single-headed made of gun metal and conforming to IS:5290.  It  shall  be complete with hand -wheel, quick coupling connection spring loaded type and blank cap.

1.12	Hose pipes, Branch Pipes and Nozzles

Hose Pipe: Hose pipe shall be rubber lined woven jacketed and 63mm in diameter.  They shall conform to type-2 (Reinforced rubber lined) of IS:639-1979.  The hose shall be sufficiently flexible and capable of being rolled.

Each run of hose pipe shall be complete with necessary coupling at the ends to match with the landing valve or with another run hose pipe or with Branch pipe.  The couplings shall be of instantaneous spring lock type.

Branch Pipe: Branch pipe shall be of gunmetal 63mm dia and be complete with male instantaneous spring lock type coupling for connection to the hose pipe.  The branch pipe shall be externally threaded to receive the nozzle.

Nozzle :  The nozzle shall be of copper or gunmetal, 20mm in internal diameter.  The screw threads at the inlet connection shall match with the threading on the branch pipe, the inlet end shall have a hexagonal head to facilitate screwing of the nozzle on to the branch pipe with nozzle spanner.

End couplings, branch pipes, and nozzles shall conform to IS:903-1985.  two hoses of 15 mtr. Lengths with couplings shall be provided with each external (yard) hydrant.  One nozzle and one branch pipe with coupling shall be provided with each yard hydrant.

1.13	External Fire Hose Cabinet

The external fire hose cabinet to accommodate the hose pipes, branch pipe nozzle and the hydrant outlets shall be fabricated from 1.5m thick sheet steel. This shall be lockable and provided with center opening glazed doors.

The support for hose cabinet shall be of brick work up to a height of 0.5m above ground level. The depth of footing for this support shall be minimum 50cm below ground level, resting on leveling course of minimum 10cm of PCC (1:5:6). The brickwork shall be plastered in cement mortar (1:6). The hose cabinet shall be painted red and stove enameled.

1.14	Internal Fire Hose Cabinet

Each internal fire hydrant valve shall be housed in a nitch of size indicated on drawings. Each internal fire hose Cabinet shall hold single headed hydrant, 2 Hoses, 2 Branch pipes and 1 no. Dunlop hose reel mounted on a drum.

- The cabinet shutters & frames shall be fabricated from boxed steel sections and MS plate 2mm thick.

B) 	The front glass of shutters shall be 5.0 mm thick clear glass and shall be held by means of rubber. Locking arrangement shall also be made with one number of mortice lock of approved make. A separate Key Box of 2 mm thick MS sheet with glass facing shall be provided.

C)	The Shutter shall be given a powder coat finish in post office red colour.

1.15	Hose Reel

The hose reel shall be directly tapped from the riser through a 25 mm dia pipe, the drum and the reel being firmly held against the wall by use of dash fasteners.  The Hose Reel shall be swinging type (180 degrees) and the entire Drum, Reel etc shall be as per IS:884. The rubber tubing shall be of approved quality and the nozzle shall be 6 mm  dia shut off type.

1.16	Brigade inlet Connections

Two sets of 4 ways collecting head Fire Brigade connection shall be provided at the location indicated in the drawing.

The inlet to the riser shall be with 150mm dia sluice valve and non-return valve.  The scope shall include providing necessary reducers, tees bends and special fittings as required.  Necessary enclosure made of 2mm thick sheet metal with support shall be provided, as in the case of hose cabinets.

2.0	Sprinkler System

2.1	Sprinkler Heads

Sprinkler heads shall be of quartzoid bulb type with bulb, valve assembly yoke and the deflector.  The sprinklers shall be approved make and type.

2.2	Types

2.2.1	Conventional Pattern

The sprinklers shall be designed to produce a spherical type of discharge with a portion of water being thrown upwards to the ceiling side of wall extras.  The sprinklers shall suitable for erection in upright position or pendant position.

A.	Spray Pattern

The spray type sprinkler shall produce a hemispherical discharge below the plane of the deflector.

B.	Ceiling (flush) Pattern

These shall be designed for use with concealed pipe work, these shall be installed pendant with plate or base flush to the ceiling with spray head below the ceiling.

- Side Wall Sprinklers

These shall be designed for installation alongwith the walls of room close to the ceiling.  The discharge pattern shall be similar to one quarter of sphere with a small proportion discharging on the wall behind the sprinklers.

2.2.2	Construction

i)	Bulb:-	Bulb shall be made of corrosion-free material strong enough to with stand any water pressure likely to occur in the system.  The bulb shall shatter when the temperature of the surrounding air reaches a predetermined level.

ii)	Valve assembly:- Water passage of the sprinkler shall be controlling assembly of flexible construction.  The valve assembly shall be held in position by the quartzoid bulb.  The assembly be stable and shall withstand pressure surges or external vibration without displacement.

iii)	Yoke:-  The yoke shall be made of high quality gun metal.  The arms of yoke shall be so designed as to avoid interference with discharge of water from the deflector.  The sprinkler body shall be coated with an approved anti corrosive treatment if the same is to used in corrosive conditions.

- Deflector:-  The deflector shall be suitable for either upright or pendent erection.  The deflector shall be designed to give an even distribution of water over the area protected by each sprinkler.

D)	Colour Code

The following colour code shall be adopted for classification of sprinkler according to nomination temperature ratings.

Sprinkler Temperature Rating 			Colour of the Bulb

68   deg. C					         Yellow

E.	Size of Sprinklers Orifices

The sprinklers shall be of 15mm nominal bore size.

2.2.3	Pipes and Fittings

Pipes for sprinkler system shall be of black steel conforming to I.S. 1239 (medium class).

Fittings for black steel pipes shall be malleable iron suitable for welding or approved type cast iron fittings with tapered screwed threads.

2.2.4	Jointing

Joint for black steel pipes and fittings shall be metal to metal tapered thread or welded joints.  A small amount of red lead may be used for lubrication and rust prevention in threaded joints.

Joints between G.I. or black steel pipes, valves and other apparatus, pumps etc. shall be made with G.I. or M.S. flanges with appropriate number of bolts.  Flanged joint shall be made with 3mm thick insertion rubber gasket.

2.2.5	Pipes Protection

All pipes above ground and in exposed locations shall be painted with one coat of red oxide primer and two or more coats of synthetic enamel paint of approved shade.

Pipes in chase or buried underground shall be painted with two coats of hot bitumen.

2.2.6	Pipe Supports

All pipes shall be adequately supported from ceiling or walls from structural clamps fabricated from M.S. structural e.g. rods, channels, angles and flats.  All clamps shall be painted with one coat of primer and two coats of black enamel paint.  The contractor shall provide inserts at the time of slab casting or anchor fastener later.

2.2.7	Valves

Sluice valves of sizes 80mm and above shall be double flanged cast iron conforming to I.S. 780.  Check valve shall be of cast iron double flanged conforming to I.S. 5312.

Valves on pipes 65mm and below shall be heavy pattern gunmetal valves with cast iron wheel seat tested to 20 kg/sqcm. pressure.  Valves shall conform to I.S. 778.

1.	Air Valves

25mm dia screwed inlet cast iron single acting air valves on all high points in the system or as shown on drawings.

2.	Drain Valves

50mm dia black steel pipe conforming to I.S. 1239 medium class with 50mm gunmetal full way valve for draining and water in the system in low pockets.

2.2.8	Installation Control Valve

Installation control valves shall comprise of the followings:

a)	One-man stop valve of full way pattern with gunmetal pointer to indicate where open/shut.

b)	One automatic alarm valve fitted with handle & cover.

c)	One hydraulic alarm motor and gong for sounding a continuous alarm upon out-break of fire.  One combined waste and testing valve including 5mtr of tubing and fittings.

d)	Alarm stops valve.

e)	Strainer

f)	Drain plug

g)	Padlock and strap

h)	Wall box for installation of valve.

I)	All other accessories as required.

2.3	Pressure Gauges

Burden type pressure gauges conforming to IS/BS specifications shall be provided at the following locations:

a.	Just above alarm valve.

b.	Just below alarm valve, on the installation stop valve.

c.	One pressure gauge on delivery side of each pump.

d.	Required number of pressure gauges on pressure tank.

2.4	Installation of Piping

a.	All above ground piping shall be installed on suitable to pipe hangers/supports as required.  The hangers shall be made of MS angles, channels etc. and painted to the required finish with suitable synthetic enamel paint.  The maximum spacing of piping supports shall be as follows:

i)	20mm to 32mm dia			2.5 mtr.

ii)	40mm to 65mm dia			3.0 mtr.

iii)	65mm & above			3.0 mtr.

Piping shall be so installed that the system can be thoroughly drained.  All the pipes shall be arranged to drain to the installation drain valve.  In case of basement and other areas where the pipe work is below the installation drain valve/auxiliary valves of the following sizes shall be provided.

20mm dia valve for pipes up to 50mm dia

25mm dia valves for 65mm dia pipe

32mm dia valves for pipes larger than 65mm dia

Piping shall be of screwed type upto 50mm diameter.  Welding of joints will be allowed for pipes of above 50mm dia.

The entire piping shall be pressure tested by hydrostatic method upto a pressure of 1.5 times the working pressure.  The piping shall be slowly charged with water so that all the air is expelled from the piping by providing a 25mm inlet with a stop cock.  The piping shall be allowed to stand full of water for a period of 2 hours and then the piping shall be put under pressure by means of manually operated test pump or by a power driven test pump.  The pressure gauges used for testing shall be accurate and shall preferably the calibrated before the testing is carried out.  All the leakage’s and defects in joints revealed during the testing shall be rectified to the entire satisfaction of the Engineer-in-charge.  The system may be tested in sections/parts as the work of erection of piping proceeds.  The piping shall with stand 1.5 times the working pressure for at least 2 hours.

3.0	Operating Sequence for the Fire Fighting System

3.1	The operating pressure in the mains is to be maintained at 7.0 kg/cm2.

3.2	The jockey pump shall start automatically the moment pressure drops to 6.5 kg/cm2 because any leakage or minor draw-off from the system and stop when the pressure reaches 6.5 kg/cm2 again.

3.3	In case, after the start of jockey pump, the pressure still keeps on falling, the main fire pump shall start at 6.0 kg/cm2 by triggering of the pressure switch.  Jockey pump shall stop when main pump starts.

3.4	In the event of electrical or mechanical failure of main fire pump to start, the diesel engine driven pump shall cut in when the pressure in the mains fall down to 5.5 kg/cm2.  The main electric pump shall then be locked out.

3.5	If within a preset period the standby pump fails to start or fails to develop adequate pressure, the control system shall shut down the standby pump and lock it out and given an audiovisual indication to that effect at the control panel.

3.6	Jockey pump shall be shut down automatically when the fire pump electric or diesel, is operating.  Necessary integration of pipe work and controls shall be provided for the purpose.  A timer may be employed where necessary to distinguish between slow fall of pressure due to system leaks and sudden fall of pressure due to fire duty by opening of valves and thus prevent parallel start up of both pressurization and fire pumps.

3.7	The control panel shall have status selection for each of the pumps for “automatic” as well as “manual” operation.

3.8	Pumps when under “manual” status shall be operated manually through relevant push buttons.

3.9	The fire pumps once started shall not be stopped automatically.

3.10	The fire pumps shall be locked out for operation both for “manual” and “automatic” operations, once the low water controls operates and furnish an audio and visual alarm on the panel the audio alarm can be silenced by accepting the alarm.  The visual alarm shall be individual for each equipment.  It shall be flashing type and on acceptance remain steady.  A reset button shall be provided for each pump for returning the pump for fire duty.

3.11	Over load or under voltage/no volt trip devices for electric fire pump shall not be provided in the starter.  LED type indication lamps to indicate the availability of power shall be provided.

3.12	Once tripped the electric fire pump shall remain locked out for operation irrespective of the position of its operational status selection switch.  Look out indication shall be available on the panel.

3.13	Return to normal operational availability shall be feasible only by manual re-set of locked out units by operation of appropriate push buttons.

3.14	When fire pumps are brought into operation an audible tone from turbine type alarm operated by water flow in the mains shall be provided to indicate the healthiness of the system.  The healthy running alarm shall not be silenced till the fire pump is shut down, but the tone may be mellowed by the operation, if required.

3.15	Alarm for failure and lock out of any pump shall distinct from “healthy” alarm.  Failure alarms shall be loud and can be silenced on acceptance.

3.16	Repeat indication of various audio and visual indications on a slave remote panel in fire control room in terminal building shall be available.  The slave Remote panel shall have indication lamps to show the status of :

a)	Power healthy in fire pump room.

b)	Jockey pump ‘ON’

c)	Main pump ‘ON’

The slave Remote panel shall also have a hooter, which shall sound in case, any pump is ‘ON’.  The slave Remote panel shall have a provision to reset the hooter with the help of a push button.

4.0	Testing

4.1	Testing on Completion of Installation

The entire system shall be tested after completion of installation as per the operating sequence specified.

4.2	Schedule of Inspection

Testing of fittings/equipments shall be carried out either at site or at works in the presence of a CLIENT/CONSULTANT’s representative given below:

1.	Pumps, motors and engine	-	Inspection by Client/Consultant at

Manufacturers works

before dispatch.

2.	Electrical panel		-	Inspection by Client/Consultant at

Manufacturers works

before dispatch.

3.	Pipes				-	Visual inspection at site

for ISI mark.

4.	Various valves			-	Visual inspection at site

for ISI mark.

5.	SFUs, MCBs etc.		-	Type test certificates.

6.	Sprinklers			-	Test certificate from

independent test

laboratories.

3.	Fire hose, hydrant,		-	Visual inspection at

extinguisher etc.			site for ISI mark.

5.0	Approvals

It shall be the responsibility of the contractor to obtain the approval of drawings and to get the installation inspected and passed by any concerned authorities, as may be necessary as per local by laws, any fee payable to the local bodies for such activities shall be reimburse by the Client/Consultant on production of receipt.

6.0	Standards and Codes

1.	IS – 1648 – 1961	Code of Practice for fire safety of 			building (general) fire fighting 			equipment and maintenance.

2.	IS – 3844 – 1966	Code of practice for installation of

internal fire hydrant.

3.	IS – 2217 – 1963	Recommendation for providing first

aid and fire fighting arrangement in

public buildings.

4.	IS – 2190 – 971	Code of practice for selection, 			installation and maintenance of portable 		first fire appliance.

5.	IS – 3589	Electrically Welded Steel pipes 			(Medium class)

6.	IS – 1239	Mild steel tubes, Tubulers and other 			wrought steel fittings (Medium class)

7.	IS – 780	C.I. Double flanges sluice valve.

8.	IS – 778	Gun Metal Valves

9.	IS – 909 – 1965	External fire hydrant (underground)

10.	IS – 5290 – 1969	Internal Landing Valve

11.	IS – 884 – 1969	First and hose reel

12.	IS – 934 – 1976	Specification for portable chemical fire 		extinguisher soda acid type.

13.	IS – 2873 – 1969	Specification for fire extinguisher for 			carbon dioxide

14.	IS – 2189 & 2109	Automatic fire alarm system or BSS 			3116.

15.			National building code

# 7.0	FIRE DETECTION AND ALARM SYSTEM

## 7.1	STANDARDS

The manufacture, identification of material and testing of equipment covered in this specification shall comply with the latest editions as on date of opening of tenders of the appropriate standards of the following.  Unless otherwise specified, Indian Standards are preferred.  All the appliances and accessories shall carry IS or International certification and shall be of approved make.

NFPA 72E Standards on automatic fire detection.

IS:2189	Code of practice for selection, installation and maintenance of automatic fire detection and alarm system.

##### IS: 823  Welding procedure

IS: 1652Batteries

IS: 694  PVC insulated cables (light duty) for working voltage upto 1100 volts.

IS: 1554 PVC insulated cables (heavy duty) for voltage upto 1100 volts.

IS: 5959Specification for polythelene insulated PVC sheathed heavy duty electric cables, voltage not exceeding 1100 V

##### IS: 5578	Guide for marking of insulated conductors

IS: 3043Code of practice for earthing.

IS: 5216Guide for safety procedures and practices in electrical work.

In case where the offer deviates from the specified standards, the tenderer shall indicate clearly in the offer the alternative standards proposed and details thereof.

Unless otherwise mentioned, all applicable codes and standards shall be of the latest editions as published by the Indian Standards and all other such as may be published by them during the tenure of the contract, and shall govern in respect of workmanship, properties of materials, installation and methods of testing.  In case where suitable Indian Standards are not available, generally accepted codes and practices as approved by CLIENT/CONSULTANT shall be adopted. Any changes or modifications directed by CLIENT/CONSULTANT shall also be incorporated by the contractor during execution of the work.

Automatic fire detection and alarm system consists of fire control panel, detectors, manual call points, hooters, isolators, response indicators, etc.  The equipment and cables of the system shall be independent of any other system in the premises and shall not be shared with any other system. The fire detection and alarm system shall be installed as per  NFPA 72E / IS-2189 code.

  - DETECTORS AND ACCESSORIES

    - Detectors

The fire detectors shall be of analogue addressable type to detect one or more characteristic of fire like smoke, heat or flame. It shall be sleek, suitable communication technique with noise immunity, built-in functional test switch, microprocessor based technology, mechanically integrated photoelectric and ionization shared volume smoke chamber, etc. All types of detectors shall be of both electronically  and manually programmable type using dip-switches or handheld programmer or from fire control panel. Reversed polarity or faulty zone wiring shall not damage the detector.  The detector shall have no moving parts of components subject to wear.  It shall be possible to test the detector in the field.  The response  of a detector shall always be clearly visible from outside by a flashing light on the base. The detector shall connect to the control unit via a fully supervised two-wire circuit. A built barrier shall prevent entry of insects into the sensor.  The detector shall be designed for fast and simple cleaning.

All electronic circuits must be solid state devices and virtually hermetically sealed to prevent their operation from being impaired by dust dirt or humidity.  All circuitry must be protected against usual electrical transients and electromagnetic interference. All radioactive parts of the source, if any,  shall be fully gold plated. The detector shall be inserted into or removed from the base by a simple push-twist mechanism to facilitate easy exchange for cleaning and maintenance.

The smoke & heat detectors shall fit into a common type standard base.  The standard base shall be supplied with a seal plate, preventing dirt, dust, condensation or water reaching the wire terminals or the detector points. Detectors shall be provided with a MS box for entry and termination of armoured cable and to protect detectors terminals.

At the time of installation and prior to commissioning, every detector shall be allotted an identification number. All detectors shall  have LED blink when it is addressed. Detectors shall not be either partially or totally recessed in ceiling or wall. Detectors shall be suitably protected where they are liable to be subjected to mechanical damage. Detectors should not be painted or coated or covered in any manner after installation as this will adversely affect the sensitive of operation.

7.2.2    Beam detectors

It shall be addressable type linear optical beam smoke detector type.  It shall be of a combined transmitter/receiver unit. The minimum range of the detector shall be 50 m. The detector shall operate in the infra – red light spectrum. Numerical indicators shall be provided to aid beam alignment. The indicators shall comply to EN 54- 12 standards. The detector shall operate on the principle of light obstruction utilizing infra-red beam. The detector shall have standby automatic fault and alarm LED indicators visible from the front and bottom. Alignment shall be  accomplished via an optical sight and it shall be listed for operation from - 22° F to 131° F. Smooth four square grid reflector shall also be provided reflect the transmitted beam shall also be provided for the satisfactory performance of the system.

7.2.3  Smoke detectors

It shall be of optical-cum-thermal type. Smoke detectors shall quickly respond to smoke containing small particles normally produced and heat likely to be generated and automatically adjusts sensitivity without needing operator intervention.

7.2.4  Heat detector

It shall be of fixed-cum-rate of rise temperature type.  Heat detectors shall be suitable for use in situation where sufficient heat is likely to be generated and damage caused by heat generated.

7.2.5.	Loop Hooters

The loop hooters shall be so arranged that when any alarm operates all the hooters through out the premises shall be activated. The hooters at the fire alarm shall be electronic type having frequency of suitable frequency range. The hooters shall be capable to produce a sound output of 90 db at 1 m. Hooters shall be of loop powered and no separate power is provided.

‘Fault’ alarm and ‘Fire’ alarm in a panel sounder shall be distinctly different. Fire alarm sounders shall not be used for any purpose other than for fire operations. When installed flush with a false ceiling these shall match the ceiling surface.  Necessary provisions such as wooden boxing or frame work, if required, to accommodate the sounders shall be made in the ceiling in advance.

These shall be installed at a height not lower than 2.4 m, except when recessed in a false ceiling of lower height.  In such cases the sounders shall be recessed at false ceiling level.

The panel sounders in the respective panels shall be actuated automatically as soon as fire alarm signal is initiated from any trigger device connected to them.  These shall also be sounded when there is a fault alarm signal within their areas of control.  The sound shall be continuous and of the same characteristics from all fire alarm sounders in a building.

7.2.6.	Loop Isolators

Loop isolators shall be designed to protect one area or a number of devices which are consecutively wired in a loop. Its function is to isolate a section of the loop if a problem develops within that section, allowing the remainder of devices connected on the loop to function correctly. Loop isolators shall be provided after every 20-30 devices in each loop.

7.2.7.	Manual Call Points (MCPs)

It shall be of ‘break glass’ type, and 1.5mm thick welded sheet steel or 3 mm thick cast aluminium. The front glass shall be breakable. The MCPs shall be recess mounted suitable to support the intelligent addressable panel.  It  shall form an integral part of the fire detector system. The housing shall be dust/vermin proof properly sealed with rubber lining.  The glass frangible element shall keep a push button pressed inside such that in the event of breaking the glass, the push button is released to actuate an alarm in the control panel.  MCPs shall be easily resetable with key.

Where sheet steel is used for, this shall be thoroughly cleaned off dust, dirt, grease and rust if any and two coats of anti rust primer shall be given both inside and outside.  This shall be followed by two coats of synthetic enamel paint in fire red colour on the external surface that will be visible on installation. In the case of cast aluminium body for a call box, the surface shall be neatly finished with red colour paint.   The following words shall be painted on the front of the call box in contrasting colour with a letter size of not less than 5mm.

“BREAK GLASS IN CASE OF FIRE”

Installation requirements:-

Manual call points shall be located at exit space and shall be installed at a height of 1.4 m above the floor at an easily accessible position. They shall be installed at easily accessible, well illuminated positions, preferably in a contrasting background so that they are easily noticable from either direction.  They may be semi-recessed so as to project by 10mm. They shall be installed free from obstructions.

## 7.2.8.  Fire Control Panel

The fire alarm control panel shall be of micro processor controlled and of modular hardware design of intelligent addressable type. It shall be housed in a steel enclosure. It shall also be finished with hard wear textured epoxy paint/ powder coated. Cable entries shall be provided on the top and bottom of the panel.

The system capacity shall be based on the number of devices  and control modules. Each devices in the system shall be identified by its unique address position on the two wire loop. The panel retains command over the alarm process, LED indicators, automatic test feature and  loop hooters. The panel shall be of software programmable. The panel shall be capable of:-

- programmable at site.

- automatic system test activates

- detector sensitivity adjustments

- alarm verification

- Alpha/numerical display

- Relay control module

- Support for bacnet and modbus protocol.

- maintenance alert facilities

- provision to connect to PCs

The panel shall have facility to shut off individual AHUs in case of fire through relay arrangements.  The relay shall be suitable to withstand AHU contactor coil current.

The manufacturer of fire control panel, detectors and other detection devices shall have own or authorized service centre in India with spares for carrying out maintenance service during the guarantee and maintenance periods.  The tenderer shall submit a brief write-up of the service centre facilities available in India along with the tender.

7.2.9    Power Supply of panel

The power supply shall drive the system from either the main electrical supply single phase supply or the standby power supply.  The standby power supply shall be derived from exclusive SMF back-up batteries of reputed make.  Standby power supply shall be capable of maintaining the system in normal operation having a period of not less than 24 hrs. after the failure of normal main supply.

### 7.2.10. Control Cable

The control cable for wiring fire alarm system shall be of 650 Volt grade.  Cables shall be laid as per relevant installation standards. The size of these cables are specified in schedule of requirements.

7.2.11  Cable Glands

Cable glands shall be of heavy duty single compression type of brass, chrome plated. These shall have a screwed nipple with conduit electrical thread and checknut. These shall be suitable for armoured/unarmoured cables, which is being used.

7.2.12  Cable Connectors

Cable connectors, lugs/sockets, shall be of copper/aluminium alloy, suitably tinned, solderless, crimping type. These shall be suitable for the cable being connected and type of function (such as power, control or connection to instruments, etc.)

# 8.    INSPECTION AND TESTING

# (Fire detection and alarm system)

## 8.1	INSPECTION

All materials shall be offered for inspection in cleaned condition, prior to erection.  At no event, site fabricated work /material shall be installed in position without inspection and approval by CLIENT/CONSULTANT.  The Contractor shall ensure that each stage of fabrication is carried out in compliance with the procedures specified in the IS standards as applicable and/or specified in this document.

The contractor shall conduct sample tests of all the materials supplied at reputed laboratories/agencies as directed by CLIENT/CONSULTANT at his own cost and test reports are to be submitted. Inspecting officials like CLIENT/CONSULTANT, TAC / Local Authorities shall have the right to access the premises of the work at any time with or without giving prior notice. All the formalities or procedures for conducting the inspections by the authorities as required by them shall be arranged by the contractor free of cost.

All testing shall be carried out in the presence of CLIENT/CONSULTANT/ statutory authorities and test registers shall be maintained by the contractor. The contractor shall provide all material, tools, equipment, instruments, services and personnel required to perform the tests and remove debris resulting from cleaning and after testing free of cost.

The original test certificates of all tests conducted are to be forwarded to  CLIENT/CONSULTANT.  After conducting the tests, any defects found on materials, equipment, piping, etc. shall be got rectified/repaired / replaced by the Contractor without any extra cost.

8.2	 TESTING

8.2.1 Fire Detection and Alarm System

The entire fire detection and alarm system shall be tested for continuity and performance as per IS-2189 code. After installation, the visual inspection of all the detectors shall be made to make sure that they are properly installed.  Each detector shall be inspected to ensure that it is properly mounted and connected.  Heat detectors shall be tested to initiate an alarm by a heat source such as hair drier or a shielded heat lamp.  After each heat test, the detectors shall be reset.  Smoke detectors shall be tested to initiate an alarm at its installed location with smoke or other aerosol.   All detectors found to have the sensibility outside the approved range shall not be used.

Detectors, control and indicating panels, sounders shall be tested at the manufacturer’s factory and test certificate be furnished with the supply. Type test certificate to prove conformity to the relevant contract specifications shall be furnished with the supply, from recognised testing institutions or Govt. test bodies in India or abroad.

Following tests shall be conducted in the presence of CLIENT/CONSULTANT and the test certificate shall be furnished with the record of tests.

8.2.2  Continuity test

Test for insulation resistance of the wiring work and the control and indicating panels.

    - Test for system operation.

Tests for detectors shall be conducted using a test fire at normal floor level. The system operation for fault conditions shall be conducted by introducing faults such as open circuit, short circuit, removal of detector, open/short circuit in a sounder circuit etc. Tests relevant to loop isolators shall also be conducted to confirm that it functions as required.

TECHNICAL  DATA

### (Fire detection and alarm system)

(To be submitted along with the tender)

Note: 	Refer list of preferred makes of items in Section IV. (Please attach catalogue, 	etc. of items from the original supplier)

Beam Detectors

Make

Model No.

Size:

Beam range:

Alignments : Horizontal & Vertical :

Reflector size:

Operating temp range:

Voltage range:

LED display status:

Air velocity:

Protocol used

IP rating

Smoke Detectors

Make

Model No.

Size:

Operating temp range:

Voltage range:

LED display status:

Air velocity:

Protocol used

IP rating

Heat Detectors

Make

Model No.

Size:

Operating temp range:

Voltage range:

LED display status:

Air velocity:

Fixed temp. set point:

Rate of rise temp:

Sensor:

Protocol used:

IP rating

Loop isolators

Make

Model No.

Spacing of isolators

Operating voltage

Temp. range

Size:

IP rating

Loop hooters

Make

Model No.

No. of tones

Sound output

IP rating

Size

MCPs

Make

Model No.

Size:

IP rating

Fire control panel

Make

Model No.

Maximum No. of programmable loops

Maximum No. of devices per panel

Maximum devices per loop

Maximum control cable length

Maximum resistance per loop

Length per loop

No. of slots for additional cards

Networking facilities

No. of auxiliary output for AHU shut off.

No. of repeater output

No. of hooters per loop

No. of isolators per loop

Operating voltage

Operating current

No. of display characters

Support for  bacnet and modbus protocol.

Size

Weight

Makes of following items

PVC insulated FRLS

armoured Cu. Cable 	:

PVC insulated armoured Cu. Cable  	:

PVC insulated FRLS cu. wire	:

PVC  conduits 		:

MS  conduits 		:

TECHNICAL  DATA

(Hydrant System)

(To be submitted along with the tender)

Note: Refer list of preferred makes of items in Section IV. (Please attach catalogue, etc. of items from the original supplier).

1   	Diesel engine driven pump

1.a  	Pump details

Make

Type

Model

Overall dimensions

Weight (Kgs)

Material

Pump casing

Impeller

Shaft sleeve

Base plate

Type and material of steel

Operating speed (R.P.M.)

Head (Mtr)

Efficiency

Performance curves (whether enclosed with the tender).

Yes/No

1.b  	Engine details

a)	Make

b)	Model

c)   	HP

d)   	RPM

e)   	SFC

Oil consumption

Weight

Overall dimension

Exhaust pipe dia

2   Battery & Battery Charger

Make of battery charger

Make of batteries

Model No. of batteries

Voltage

AH

No. of batteries

Model No. of battery charger

3  	Electric motor driven pump

1.a 		Pump details

Make

Type

Model

Overall dimensions

Weight (Kgs)

Material

Pump casing

Impeller

Shaft sleeve

Base plate

Type and material of steel

Operating speed (R.P.M.)

Head (Mtr)

Efficiency

Performance curves (whether enclosed with the tender).

Yes/No

1.b  		Motor details

a)	Make

b)	Model

c)   	HP

RPM

Weight

Overall dimension

Class of insulation

4	Jockey pump

1.a  	Pump details

Make

Type

Model

Overall dimensions

Weight (Kgs)

Material

Pump casing

Impeller

Shaft sleeve

Base plate

Type and material of steel

Operating speed (R.P.M.)

Head (Mtr)

Efficiency

Performance curves (whether enclosed with the tender).

Yes/No

1.b  	Motor details

a)	Make

b)	Model

c)   	HP

d)   	RPM

g)	Weight

h)	Overall dimension

i)	Class of insulation

5	Makes and model numbers of following items

MS Pipe           	:

GI & MS fittings   	:

Valves       		:

Strainer           	:

Instrumentation    	:

Pressure guage     	:

Pressure switch    	:

Hardware           	:

Paint           	 	:

Polymeric mix      	:

Hydrant valve	:

CP hose		:

Branch pipe		:

Hose	Reel		:

TECHNICAL  DATA

(Sprinkler system)

(To be submitted along with the tender)

Note: Refer list of preferred makes of items in Section IV. (Please attach catalogue, etc. of items from the original supplier).

Alarm valve

Make

Model No.

Size

Sprinklers

Make

Model No.

Size

‘Y’ strainer

Make

Model No.

Size

MS pipes

Make

Model No.

APPROVED MAKES OF ITEMS

HYDRANT/SPRINKLER/DETECTION/SYSTEMS

Motor          	: Kirloskar/Siemens/ABB/Cromption Greaves

Pump               	: Kirloskar/Mather & Platt/KSB/Beacon/Grundfoss

Diesel Engine	: Kirloskar/Cummins/Greaves

GI/MS Pipe           	: Tata/Jindal/SAIL/GST/Zenith

GI & MS fittings   	: Tube weld/Tube products/Punjab steel/TNT

Valves	: Kirloskar / Kalpana / Updhaya / Leader / Advance

Strainer           	: Sant/Emerlad/Teleflo/Jaypee/Grandpix

Pressure guage     	: Fiebig/H.Guru

Pressure switch    	: Indfoss/Switzer/Schneider

Hydrant valve & 		: Newage/Steelage/ Arihant/Shah Bhogilal

Fire brigade point		: Newage/ Arihant/Shah Bhogilal

Branch pipe 		: Newage/ Arihant/Shah Bhogilal

CP hose		: Newage/Shah Bhogilal/Pyroline

Hose Reel	: Newage/Chathariya/Shah Bhogilal

Hose cabinet	: Newage/ Zenith/Shah Bhogilal

Hardware           	: TATA/Sundaram fasteners/GKW

Paint            	: Asian/ICI/Nerolac/Berger

Polymeric mix      	: IWL/Shalimar

Fire extinguisher	: Ceasefire/Minimax/Safex/Bharat/Safeguard.

Alarm valve		: HD / Tyco (UL listed)

Sprinkler		: HD/ Tyco  (UL listed)

Flexible pipe		: Any UL listed

Alarm System (All shall be UL/EN approved)

Smoke/heat detectors 		: Edwards/Morely/Essar/Siemens/Notifier

Fire alarm panel/Loop isolator	: Edwards/Morely/Essar/Siemens/Notifier

Hooters/Manual call points	: Edwards/Morely/Essar/Siemens/Notifier

FRLS Cable		: Havells/Finolex/Polycab/RR Kabel

BILL OF QUANTITIES