TENDER

FOR

ADDITIONAL WORKS AT DH MANANTHAVADI IN WAYANADU DIST.

PART-III

PRICE BID

TENDER NO. HLL/ID/14/5

January 2014

HLL LIFECARE LIMITED

INFRASRTUCTURE DEVELOPMENT DIVISION

CONTENTS

| S.NO | ITEM | PAGE NO. |
| --- | --- | --- |
| 1. 2. 3. | Commercial Conditions Special Conditions Bill of Quantities | 2-4 5 6 |

- COMMERCIAL CONDITIONS

    - The tendered rate shall inter alia be deemed to include for the provision of all materials, process, operation and special requirements detailed in the particular specification irrespective of whether these are mentioned in the description of equipment schedule and Bill of quantities or not. It is an express condition of the contract that the tendered rates for various items in the Bill of Quantities shall be deemed to include for the full, entire and final condition of the contractor respective items of the works in accordance with the provision of the contract.

    - The tendered rate shall include for all taxes, duties, etc. as applicable and shall be quoted on the works contract basis for the Additional works at DH Mananthavadi in Wayanadu Dist.. The tendered rate shall remain firm and free from variation due to rise in the cost of materials/equipment, labour or any other reasons whatsoever during the contract period and valid extension on the case may be.

    - The quantum of excise duty included in the tendered price, the rate at which they were assumed etc. shall be indicated in the tender.

1.1	UNIT RATES

1.12 Only approved work will be measured on completion and priced as per rates quoted           against the respective items.

1.2	BRIEF DESCRIPTION OF PRICING

1.2.1.	Unforeseen difficulties for which provision has not been made in the tender will in no way relieve the successful tenderer from the full execution of the work.

    - The price quoted shall be the final amount for this finished work.

    - The quoted price shall be inclusive of all taxes and duties whether payable by the contractor or to be deducted at source. This shall include those applicable among VAT, Sales Tax, Income Tax, Customs Duty, Excise Duty, Turnover Tax, Service Tax, Work Contract Tax, Octroi, Labour Welfare Cess or any other Taxes and Duties prevailing in respect of this contract. ANY BID STATING THAT TAXES ARE EXTRA WILL BE SUMMARILY REJECTED.

  - INCOME TAX

Any payment to the contractor as per contract will be made after deducting income tax as per the rules and regulations.

  - SALES TAX AND EXCISE DUTY

The tenderer shall clearly indicate sales tax, Excise and other duties as applicable in his offer for carrying out this work.

1.6.    SUBMISSION OF BILL

1.6.1.	The contractor shall from time to time prepare and submit interim bills of the work executed and on completion of the contract, he shall prepare and submit the final bill. The measurements sheets in support of the interim and final bills shall be prepared by the contractor on the basis of measurements taken by him jointly with the project engineer and the said measurement sheets shall be submitted by him with the relevant bill.

1.6.2.	Within the above frame work of the terms of payment the contract’s interim bills will have to be of a minimum value of Rs.25.00 Lakhs  only.

1.7.    EXTRA ITEMS

The contractor is bound to carry out any items of work necessary for the completion of the job even though such items may not have been included in the schedule of probable quantities or rates, such items being necessary or essential for completing the job. Variation order in respect of such additional items and their quantities will be issued in writing by the employer.

    - All shavings, cuttings and other rubbish as it accumulates from time to time during the progress of work and on completion including that of the sub-contractors and special tradesman and all materials condemned by the project engineer shall be cleared and removed from the site by the contractor without any extra charge.

    - All measuring steel taps, scaffolding, ladders instruments and tools that may be            required for taking measurements shall be supplied by the contractor.

- 1.8.   OVER TIME WORK

If the contractor is required to work night or on holidays in order to maintain the time schedule he shall take prior approval from the Engineer-in-charge. He should also provide and maintain at his own cost sufficient lights as may be necessary to enable the work to proceed satisfactorily during the night.

1.8.1. The contractor shall give full facilities to all other contractors working on site. He   shall also arrange his programme of work so as not hinder the progress of other trades. The decision of the Engineer-in-charge on any point of dispute between the various parties shall be final and binding.

- 1.8.2. It is specifically pointed out that the contractor shall not be entitled to any compensation whatsoever on account of delay in procurement or supply of controlled materials and the rates quoted in the contract are fixed till the completion of the contract.

- 1.8.3. The contractor shall co-operate with other agencies appointed by the owners for the work to proceed smoothly with the least possible delay and to the satisfaction of the owners, architects and the consultants.

- 1.8.4. The owners shall provide a source for power supply at one convenient point at site. The contractor shall at his own cost install a separate meter at the said source and lay additional cables from the said source also at his own cost. For the electricity consumed by the contractor he shall pay the owner the actual cost at the rate charged by the local authority for power for constructional purposes. The contractor shall also obtain the necessary permit for utilizing power for constructional purposes.

- SPECIAL CONDITIONS

2.1.    EXECUTION OF WORK

2.1.1.	The whole of the work as described in the contract (including bills of materials, specification and all drawings pertaining thereto) and as advised by the Engineer-in-charge from time is to be carried out and completed in all parts to the entire satisfaction of the Employer. Any minor details of construction which are obviously and fairly intended, or which may not have been definitely referred to in this contract, but which are usual construction practice and essential to the work, shall be included in this contact.

2.2.	CERTIFICATE OF COMPLETION

2.2.1	The contractor shall intimate to the Engineer-in-charge in writing as and when the works are completed and put into beneficial use in order to enable the consultants to check certify to the owners to take over the plants.

2.2.2	The work shall not be considered as completed and put into beneficial use until the consultants have certified in writing that the same has been completed and put into beneficial use.

2.2.3	The defects liability period shall commence from date of such completion or any specific date mentioned therein.

BILL OF QUANITIES

ABSTRACT

| SEC. | DESCRIPTION OF ITEM |  | AMOUNT (Rs.) |
| --- | --- | --- | --- |
|  | CIVIL WORKS |  |  |
| Part I | CIVIL WORKS- SURGICAL BLOCK |  |  |
| Part II | CIVIL WORKS- MATERNITY BLOCK |  |  |
| Part III | CIVIL WORKS- FRONT YARD BLOCK |  |  |
| Part IV | CIVIL WORKS-LIFT SHAFT WORK |  |  |
| Part V | CIVIL WORKS-KHRWS PAY WARD |  |  |
| Part VI | CIVIL WORKS-CONNECTING PASSAGE |  |  |
|  | ELECTRICAL WORKS & ELECTRO MECHANICAL WORK |  |  |
| Part I A | ELECTRICAL WORKS -SURGICAL BLOCK |  |  |
| Part II A | ELECTRICAL WORKS -MATERNITY WARD |  |  |
| Part III A | ELECTRICAL WORKS - KHRWS PAYWARD |  |  |
| Part IVA | SITC OF DG SET |  |  |
| Part V A | SITC OF FIRE ALARM-MATERNITY WARD |  |  |
| Part V B | SITC OF FIRE ALARM-SURGICAL BLOCK |  |  |
| Part VI A | HVAC - MATERNITY WARD |  |  |
| Part VI B | HVAC - SURGICAL BLOCK |  |  |
| Part VIII A | MEDICAL GAS –SURGICAL & GYNAEC |  |  |
|  | GRAND TOTAL |  |  |

| ADDITIONAL WORKS AT DISTRICT HOSPITAL AT MANANTHAVADI IN WAYANAD DISTRICT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| PART I CIVIL WORK SURGICAL BLOCK |  |  |  |  |  |
| SL No | Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| I | SUB HEAD -I - DEMOLISHING ANG DISMANTLING |  |  |  |  |
| 1 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. | cum | 6.00 |  |  |
| 2 | Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional area of R.C.C. or R.B. work) as per direction of Engineer - in -charge | sqm | 45.00 |  |  |
| 3 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge- in cement morter | cum | 5.00 |  |  |
| II | SUB HEAD - II - REINFORCED CEMENT CONCRETE |  |  |  |  |
| 4 | Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size) | cum | 0.30 |  |  |
| 5 | Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL) | kg | 50.00 |  |  |
| III | SUB HEAD - III - BRICK WORK |  |  |  |  |
| 6 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand | cum | 5.00 |  |  |
| IV | SUB HEAD -IV- STEEL WORK |  |  |  |  |
| 7 | Steel work in built up tubular ( round, square or rectangular hollow tubes etc.) trusses etc. including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete.Hot finished welded type tubes | kg | 1270.00 |  |  |
| V | SUB HEAD --V -- Aluminium Work |  |  |  |  |
| 8 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion Powder coated Aluminium (minimum thickness of powder coating 50 micron) | kg | 115.00 |  |  |
| 9 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately):For shutters of doors, windows & ventilators including providing and fixinghinges / pivots and making provision for fixing of fittings wherever requiredincluding the cost of EPDM rubber / neoprene gasket required (Fittings shall bepaid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron | kg | 186.00 |  |  |
| 10 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. | each | 8.00 |  |  |
| 11 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With OPAC glass panes of 4.0 mm thickness | sqm | 20.00 |  |  |
| 12 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | sqm | 15.00 |  |  |
| 13 | Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in chargePre laminated particle board with decorative lamination on both sides | sqm | 10.00 |  |  |
| 14 | Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete | each | 14.00 |  |  |
| 15 | Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper | each | 35.00 |  |  |
| 16 | providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm | each | 15.00 |  |  |
| 17 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge.Powder coated minimum thickness 50 micron aluminium tubular handle bar. | each | 30.00 |  |  |
| 18 | Extra for providing and fixing aluminium grill of approved make and manufacture (Dura grill or equivalent) made up of 5mm dia aluminium rod and apparture of 50mmx50mmm fixed with aluminium frame as directed by the engineer in charge. | sqm | 65.00 |  |  |
| VI | SUB HEAD -VI - FLOORING WORKS |  |  |  |  |
| 19 | Providing and fixing homogeneous antistatic Polyvinyl chloride sheet roll from fused jointed in flooring and skirting in approved pattern on a smooth and damp proof base using rubber based adhesives of approved quality and manufacturer like Dunlop S-758, Fevicol SR 998, Pidilite or equivalent as per IS 3462,BS 2050 & BS 3261 including rolling with light wooden roller weighing about 5 kg and having surface resistance in the range of 4x104Ω- 5x108 Ω all complete as directed by Engineer-in-charge, in approved colour and shade.- Pidilite Roffler anstistatic SL or equivalent. .2 mm Thick sheet | sqm | 260.00 |  |  |
| 20 | Providing and applying self levelling material for leveland smooth uneven internal sub-floors such as concrete,cement/sand screed, quarry iles, etc. prior to the installation of resilient flooring using ARDEX CL 11 as directed by the Engineer-in charge | sqm | 260.00 |  |  |
| 21 | Provinding and applying priming coat using ARDEX P51 as a bonding agent on absorbent cement/sand screeds prior to applying ARDEX sub-floor smoothing compoundsas directed by the Engineer-in charge | sqm | 260.00 |  |  |
| VII | SUB HEAD -VII -ROOFING WORKS |  |  |  |  |
| 22 | Providing and fixing at all heights false ceiling of 8mm thick PVC hollow sheet including providing and fixing of frame work made of special section power pressed from MS sheet and galvanazied in accordance with zinc coating as per IS :277 and consisting of angle cleat of size 25mm wide x 1.6mm thick with flanges of 22mm and 37mm at1200mm c/c one flange fixed to the ceiling with dash fastner 12.5mm dia x 40mm long with 6mm dia bolts to the angle hangers of (25x25x0.50)mm of required length and other end of the angle hanger being fixed with nuts &bolts to GI channels (45 x 15 x 0.90 )mm running at the rate of 1200mm c/c to which the ceiling section 0.5mm thick bottom wedge of 80mm with tapered flanges of 26mm each having clips of 10.5mm at 450mm c/c shall be fixed in a direction perpendicular to |  |  |  |  |
|  | GI chanel with connecting clips made out of 2.64mm dia x 230mm long with GI wire at every junction including fixing the PVC sheet with ceiling section and perimeter chanel 0.50mm thick 27mm high having flanges of 20mm and 30mm long, the perimeter of ceiling fixed to25mm long drive-all screws @ 230mm interval including jointing and fixing to a flush finish of square edges of the board with recommended filler, jointing tapes, finisher and two coats of primer suitable for board as per manufactures specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed all complete as per drawing and specification and direction of the Engineer in Charge but excluding the cost of painting | sqm | 38.00 |  |  |
| 23 | Providing & Fixing of Armstrong Clip-in swing down plain finish metal ceiling System consisting of 600x600 mm clip in tiles of pre coated Aluminium in 0.7mm thickness with bevel edge in white colour (RAL 9010) with Light Reflectance > 86% and suitable for Green Building application, with Recycled content of 50%. | sqm | 170.00 |  |  |
|  | Installation: To comprise 3000mm long ‘C’ channels spaced at 1200mm centres securely fixed to the structural soffit by support clamp & approved hangers. The last hanger at the end of each C channel should not be greater than 600mm from the adjacent wall. Use a C-channel connector for splicing two pieces of C-channels. 4000mm Dp-12 Main carriers (spring tee bars) shall be spaced at 600mm centres in a direction perpendicular to the C-channels and shall be secured at every intersection with C channel using a dp-12 hanger. Use Dp-12 connector to splice two pieces of Dp-12 main carriers.Tiles should be clipped in between two Dp-12 carriers (spring tee bars) from below. |  |  |  |  |
| VIII | SUB HEAD -VIII -FINISHING WORKS |  |  |  |  |
| 24 | 12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand) | sqm | 51.00 |  |  |
| 25 | Extra for plastering on circular work not exceeding 6 m in radius:In two coats | Sqm | 43.00 |  |  |
| 26 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm | Sqm | 51.00 |  |  |
| IX | SUB HEAD -IX -SANITARY INSTALLATION WORKS |  |  |  |  |
| 27 | Providing and fixing stainless steel scrub 1200x400x600mm with C.I brackets and stainless steel plug 40mm including painting of fittings and brackets ,cutting and making good the walls wherever required a)Scrub with drain board | Each | 1.00 |  |  |
| 28 | Providing and fixing C.P towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality ,size and make | Each | 2.00 |  |  |
| 29 | Providing and fixing S.S soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | Each | 2.00 |  |  |
| 30 | Providing and jointing PVC 63mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 63mm diameter (OD) | rm | 30.00 |  |  |
| 31 | Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete. |  |  |  |  |
|  | 25mm PVC pipe (10kg/sqcm) | rm | 30.00 |  |  |
| 32 | Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors: 110mm inlet and 110mm outlet pvc | Each | 1.00 |  |  |
| 33 | Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square,100mm diameter of the inner hinged round grating. Rectangular type with circular round lid | Each | 1.00 |  |  |
| 34 | Providing and fixing C.P brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. 15 mm nominal bore With long Handle | Each | 4.00 |  |  |
| 35 | Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) – |  |  |  |  |
|  | 25mm PVC pipe (10kg/sqcm) | Each | 2.00 |  |  |
| 36 | Providing and fixingpvc 10 kg bend of specified diamenter including cutting and finishing etc.complete |  |  |  |  |
|  | 63mm PVC pipe (10kg/sqcm) | Each | 15.00 |  |  |
|  | TOTAL PART I - CIVIL WORK |  |  |  |  |

| TOTAL PART II CIVIL WORK - METERNITY BLOCK |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SL No | Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| I | SUB HEAD -I - DEMOLISHING ANG DISMANTLING |  |  |  |  |
| 1 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. | cum | 2.00 |  |  |
| 2 | Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional area of R.C.C. or R.B. work) as per direction of Engineer - in -charge | sqm | 2.00 |  |  |
| 3 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge | cum | 3.00 |  |  |
| 4 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :Of area beyond 3 sq. metres | sqm | 3.00 |  |  |
| II | SUB HEAD - II - REINFORCED CEMENT CONCRETE |  |  |  |  |
| 5 | Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size) | cum | 0.20 |  |  |
| 6 | Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL) | kg | 25.00 |  |  |
| III | SUB HEAD - III - BRICK WORK |  |  |  |  |
| 7 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand | cum | 1.00 |  |  |
| 8 | Half Brick masonry with FPS bricks of class designation 75 in superstructure above plinth level upto floor V level in cement mortar 1:4 (1 cement: 4 coarse sand) | Sqm | 6.00 |  |  |
| 9 | Extra providing and placing in position 2 nos.6mm dia MS bars at every third course of half brick masonry (with F P S Bricks) | Sqm | 6.00 |  |  |
| IV | SUB HEAD --IV -- Aluminium Work |  |  |  |  |
| 10 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion powder coated Aluminium (minimum thickness of powder coating 50 micron) | kg | 135.00 |  |  |
| 11 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately):For shutters of doors, windows & ventilators including providing and fixinghinges / pivots and making provision for fixing of fittings wherever requiredincluding the cost of EPDM rubber / neoprene gasket required (Fittings shall bepaid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron | kg | 90.00 |  |  |
| 12 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. | each | 5.00 |  |  |
| 13 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With OPAC glass panes of 4.0 mm thickness | sqm | 3.00 |  |  |
| 14 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | sqm | 15.00 |  |  |
| 15 | Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in chargePre laminated particle board with decorative lamination on both sides | sqm | 40.00 |  |  |
| 16 | Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete | each | 3.00 |  |  |
| 17 | Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper | each | 8.00 |  |  |
| 18 | providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm | each | 8.00 |  |  |
| 19 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge.Powder coated minimum thickness 50 micron aluminium tubular handle bar. | each | 4.00 |  |  |
| V | SUB HEAD -V - FLOORING WORKS |  |  |  |  |
| 20 | Providing and fixing homogeneous antistatic Polyvinyl chloride sheet roll from fused jointed in flooring and skirting in approved pattern on a smooth and damp proof base using rubber based adhesives of approved quality and manufacturer like Dunlop S-758, Fevicol SR 998, Pidilite or equivalent as per IS 3462,BS 2050 & BS 3261 including rolling with light wooden roller weighing about 5 kg and having surface resistance in the range of 4x104Ω- 5x108 Ω all complete as directed by Engineer-in-charge, in approved colour and shade.- Pidilite Roffler anstistatic SL or equivalent. .2 mm Thick sheet | sqm | 145.00 |  |  |
| 21 | Providing and applying self levelling material for leveland smooth uneven internal sub-floors such as concrete,cement/sand screed, quarry iles, etc. prior to the installation of resilient flooring using ARDEX CL 11 as directed by the Engineer-in charge | sqm | 145.00 |  |  |
| 22 | Provinding and applying priming coat using ARDEX P51 as a bonding agent on absorbent cement/sand screeds prior to applying ARDEX sub-floor smoothing compoundsas directed by the Engineer-in charge | sqm | 145.00 |  |  |
| 23 | Providing and fixing at all heights false ceiling of 8mm thick PVC hollow sheet including providing and fixing of frame work made of special section power pressed from MS sheet and galvanazied in accordance with zinc coating as per IS :277 and consisting of angle cleat of size 25mm wide x 1.6mm thick with flanges of 22mm and 37mm at1200mm c/c one flange fixed to the ceiling with dash fastner 12.5mm dia x 40mm long with 6mm dia bolts to the angle hangers of (25x25x0.50)mm of required length and other end of the angle hanger being fixed with nuts &bolts to GI channels (45 x 15 x 0.90 )mm running at the rate of 1200mm c/c to which the ceiling section 0.5mm thick bottom wedge of 80mm with tapered flanges of 26mm each having clips of 10.5mm at 450mm c/c shall be fixed in a direction perpendicular to |  |  |  |  |
|  | GI chanel with connecting clips made out of 2.64mm dia x 230mm long with GI wire at every junction including fixing the PVC sheet with ceiling section and perimeter chanel 0.50mm thick 27mm high having flanges of 20mm and 30mm long, the perimeter of ceiling fixed to25mm long drive-all screws @ 230mm interval including jointing and fixing to a flush finish of square edges of the board with recommended filler, jointing tapes, finisher and two coats of primer suitable for board as per manufactures specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed all complete as per drawing and specification and direction of the Engineer in Charge but excluding the cost of painting | sqm | 70.00 |  |  |
| 24 | Providing & Fixing of Armstrong Clip-in swing down plain finish metal ceiling System consisting of 600x600 mm clip in tiles of pre coated Aluminium in 0.7mm thickness with bevel edge in white colour (RAL 9010) with Light Reflectance > 86% and suitable for Green Building application, with Recycled content of 50%. | sqm | 51.00 |  |  |
|  | Installation: To comprise 3000mm long ‘C’ channels spaced at 1200mm centres securely fixed to the structural soffit by support clamp & approved hangers. The last hanger at the end of each C channel should not be greater than 600mm from the adjacent wall. Use a C-channel connector for splicing two pieces of C-channels. 4000mm Dp-12 Main carriers (spring tee bars) shall be spaced at 600mm centres in a direction perpendicular to the C-channels and shall be secured at every intersection with C channel using a dp-12 hanger. Use Dp-12 connector to splice two pieces of Dp-12 main carriers.Tiles should be clipped in between two Dp-12 carriers (spring tee bars) from below. |  |  |  |  |
| VI | SUB HEAD -VI -FINISHING WORKS |  |  |  |  |
| 25 | 12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand) | sqm | 20.00 |  |  |
| 26 | Extra for plastering on circular work not exceeding 6 m in radius:In two coats | Sqm | 45.00 |  |  |
| 27 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm | Sqm | 20.00 |  |  |
| 28 | Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete | Sqm | 145.00 |  |  |
| VII | SUB HEAD -VII -INTERNAL WATER SUPPLY & SANITORY INSTALLATIOS |  |  |  |  |
| 29 | Providing and fixing stainless steel scrub 1200x400x600mm with C.I brackets and stainless steel plug 40mm including painting of fittings and brackets ,cutting and making good the walls wherever required a)Scrub with drain board | Each | 1.00 |  |  |
| 30 | Providing and fixing C.P towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality ,size and make | Each | 2.00 |  |  |
| 31 | Providing and fixing S.S soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | Each | 2.00 |  |  |
| 32 | Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete. |  |  |  |  |
|  | 25mm PVC pipe (10kg/sqcm) | rm | 15.00 |  |  |
| 33 | Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors: 110mm inlet and 110mm outlet pvc | Each | 1.00 |  |  |
| 34 | Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square,100mm diameter of the inner hinged round grating. Rectangular type with circular round lid | Each | 1.00 |  |  |
| 35 | Providing and fixing C.P brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. 15 mm nominal bore With long Handle | Each | 4.00 |  |  |
| 36 | Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) – |  |  |  |  |
|  | 25mm nominal bore | Each | 2.00 |  |  |
| 37 | Providing and fixingpvc 10 kg bend of specified diamenter including cutting and finishing etc.complete |  |  |  |  |
|  | 63mm PVC pipe (10kg/sqcm) | nos | 5.00 |  |  |
|  | TOTAL PART II- CIVIL WORK |  |  |  |  |

| TOTAL PART III- CIVIL WORK - FRONT YARD WORK |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SL No | Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| I | SUB HEAD -I - DEMOLISHING ANG DISMANTLING |  |  |  |  |
| 1 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge | cum | 3.00 |  |  |
| 2 | Demolishing stone rubble masonry manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge: In cement mortar. | Cum | 5.00 |  |  |
| 3 | Dismantling steel work in built up sections in angles, tees, flats and channels including all gusset plates, bolts, nuts, cutting rivets, welding etc. including dismembering and stacking within 50metres lead. | kg | 165.00 |  |  |
| 4 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles 10 mm to 25 mm | sqm | 15.00 |  |  |
| II | SUB HEAD -II - EARTH WORK |  |  |  |  |
| 5 | Earth work in excavation by mechanical means (Hydraulic Excavator )/ manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | cum | 78.00 |  |  |
| 6 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | cum | 55.00 |  |  |
| III | SUB HEAD - III - PLAIN CEMENT CONCRETE |  |  |  |  |
| 7 | Cement concrete(Cast-in-situ) Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering- All work upto plinth level 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40mm nominal size) | cum | 12.00 |  |  |
| 8 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor,etc., up to floor five level, excluding the cost of centering, shuttering and finishing 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) | cum | 15.00 |  |  |
| 9 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) | cum | 2.00 |  |  |
| IV | SUB HEAD - IV - REINFORCED CEMENT CONCRETE |  |  |  |  |
| 10 | Providing and laying in position specified grade of reinforced cement concrete including the cost of centering,shuttering,finishing and excluding cost of reinforcment -All work upto plinth level. 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size | cum | 6.00 |  |  |
| 11 | Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL) | kg | 750.00 |  |  |
| V | SUB HEAD - V- STONE WORK |  |  |  |  |
| 12 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) at plinth level with: Cement mortar 1:6 (1 cement : 6 coarse sand) | cum | 68.00 |  |  |
| V | SUB HEAD - V - BRICK WORK |  |  |  |  |
| 13 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand | cum | 8.00 |  |  |
| VI | SUB HEAD -VI -FINISHING WORKS |  |  |  |  |
| 14 | 12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand) | sqm | 56.00 |  |  |
| 15 | 15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement :4 fine sand) | Sqm | 72.00 |  |  |
| 16 | Pointing on stone work with cement mortar 1:3 (1 cement: 3 fine sand) :Flush/ Ruled pointing | sqm | 54.00 |  |  |
| 17 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm | Sqm | 72.00 |  |  |
|  | SUB HEAD -VII - FLOORING WORKS |  |  |  |  |
| 18 | Chequered terrazo tiles 22 mm thick with graded marble chips of size up to 6 mm in floors, jointed with neat cement slurry mixed with pigment to match the shade of the tiles including rubbing and polishing complete, on 20 mm thick bed of cement mortar 1:4 (1 cement :4 coarse sand); light shade using white cement | Sqm | 13.00 |  |  |
| 19 | Providing and laying 60mm thick factory made cement concrete interlocking paver blocks of M - 30 grade made by block making machine with strong vibratory compaction and of approved size and design/ shape laid in required colour and pattern over and including 50mm thick compacted bed of coarse sand, filling the joints with coarse sand etc all complete as per the direction of Engineer in charge. | Sqm | 625.00 |  |  |
| 20 | Providing & fixing weepholes in RR masonry works using 63mm Pvc (6kg/cm2) | Each | 40.00 |  |  |
|  | TOTAL PART III- CIVIL WORK |  |  |  |  |

| TOTAL PART IV- CIVIL WORK - METERNITY BLOCK -LIFT SHAFT |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| SL No | Description |  | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| I | SUB HEAD -I - DEMOLISHING ANG DISMANTLING |  |  |  |  |  |
| 1 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge |  | cum | 4.20 |  |  |
| 2 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :Of area 3 sq. Metres and below |  | sqm | 2.50 |  |  |
| II | SUB HEAD -II - EARTH WORK |  |  |  |  |  |
| 3 | Earth work in excavation by mechanical means (Hydraulic Excavator )/ manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. |  | cum | 33.00 |  |  |
| 4 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. |  | cum | 13.00 |  |  |
| 5 | Supplying and providing interlocking sheet piles to the sides of the trenches with interlocking sheet piles supplied, driven down vertically one after another to line and levels with suitable pile driving equipments and accessories up to a maximum depth of 1 m below the bottom of the proposed excavation and extending 50 cm above the ground level suitably with walling pieces with 6 mm thick sheet piles of 4.25 m length installed with M.S channels on 175 mmx90mm RS joist @ 19.3 kg/mt placed and at fastened to the pile wall suitably and struting with wooden joists for hard wood or M.S screw jacks fixed at 2.5 m intervals and maintaining the shoring till the retaining wall is casted and cured and trenches are back filled including conveyance of tools and plants and other materials equipments and all other incidental charges like cleaning of sheet piles and other interlocking arrangements before driving etc dismanting and cleaning restacking for reuse including all abour and hire charges and conveyance of equipments tools and other sundries etc complete |  | sqm | 27.00 |  |  |
| III | SUB HEAD - III - PLAIN CEMENT CONCRETE |  |  |  |  |  |
| 6 | Cement concrete(Cast-in-situ) Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering- All work upto plinth level 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40mm nominal size) |  | cum | 1.50 |  |  |
| IV | SUB HEAD - IV - REINFORCED CEMENT CONCRETE |  |  |  |  |  |
| 7 | Providing and laying in position specified grade of reinforced cement concrete including the cost of centering,shuttering,finishing and excluding cost of reinforcment -All work upto plinth level. 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size |  | cum | 9.00 |  |  |
| 8 | Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) |  | cum | 5.00 |  |  |
| 9 | Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size) |  | cum | 11.00 |  |  |
| 10 | Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL) |  | kg | 3400 |  |  |
| V | SUB HEAD - V - BRICK WORK |  |  |  |  |  |
| 11 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand |  | cum | 20.00 |  |  |
| 12 | Half Brick masonry with FPS bricks of class designation 75 in superstructure above plinth level upto floor V level in cement mortar 1:4 (1 cement: 4 coarse sand) |  | Sqm | 5.00 |  |  |
| 13 | Extra providing and placing in position 2 nos.6mm dia MS bars at every third course of half brick masonry (with F P S Bricks) |  | Sqm | 5.00 |  |  |
| VI | SUB HEAD -VI- STEEL WORK |  |  |  |  |  |
| 14 | Providing and fixing M.S grills of required pattern in frames of windows etc with M.S.flats,square or round bars etc all complete:-Fixed to openings/wooden frames with rawl plugs screws etc |  | Kg | 230.00 |  |  |
| VII | SUB HEAD -VII-FINISHING WORKS |  |  |  |  |  |
| 15 | 12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand) | sqm |  | 135.00 |  |  |
| 16 | 6mm cement plaster to ceiling of mix 1 : 3 (1 cement : 3 fine sand ) | sqm |  | 40.00 |  |  |
| 17 | 15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement :4 fine sand) | Sqm |  | 155.00 |  |  |
| 18 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm | Sqm |  | 175.00 |  |  |
| 19 | Finishing walls with Acrylic Smooth exterior paint of required shade: —New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including basecoat of water proofing cement paint applied @ 2.20 kg/ 10 sqm) | Sqm |  | 155.00 |  |  |
| 20 | Steel Work painting- Painting with synthetic enamel paint of approved brand and manufacture to give an even shade. Two or more coats on new work | Sqm |  | 15.00 |  |  |
| 21 | Providing and fixing 18mm thick gang saw cut mirror polished (premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size of approved shade, colour and texture laidover 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing moulding and polishing to edge to give high gloss finish etc. complete at all levels.Granite of any colour & Shade. area of slab over 0.50 sqm | sqm |  | 10.00 |  |  |
| 22 | Providing edge moulding to 18mm thick marble stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge. | rm |  | 65.00 |  |  |
| 23 | Providing and laying polished vitrified floor tiles of minimum size 600x600mm of thickness 10mm or nearest size of M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent in light colours and shades, with water absorption's less than 0.08% and conforming to IS:15622, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with cement and matching pigments etc, complete as directed by the Engineer-in-charge. (Basic price not less than 865/m2) | Sqm |  | 16.00 |  |  |
| 24 | Providing and fixing in position polyurethane sealant including cost of primer, sealing compound in expansion joints. | rm |  | 15.00 |  |  |
| 25 | Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : (a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours (b) Second layer of slurry of cement @ 0.242 kg/sqm mixed with water proofing cement compound @ 0.126 kg/sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours The rate includes preparation of surface, treatment and sealing of all joints,corners, junctions of pipes and masonry with polymer mixed slurry. | sqm |  | 25.00 |  |  |
|  | TOTAL PART IV- CIVIL WORK |  |  |  |  |  |

| TOTAL PART V- CIVIL WORK- KHRWS PAY WARD |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SL No | Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| I | SUB HEAD -I -FINISHING WORKS |  |  |  |  |
| 1 | Cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of neat cement,20mm cement plastering | sqm | 365.00 |  |  |
| 2 | Extra for providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers. | Per bag of 50 kg cement used | 40.00 |  |  |
| 3 | Wall painting with plastic emulsion paint of approved brand and manufacture to give an even shade : One or more coats on old work. | sqm | 2200.00 |  |  |
| 4 | Finishing walls with Acrylic Smooth exterior paint of required shade: —Old work (Two or more coat applied @ 1.67 ltr/ 10 sqm) on existing cement paint surface | Sqm | 670.00 |  |  |
| 5 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade : One or more coats on old work. | sqm | 28.00 |  |  |
| II | SUB HEAD -II - DRAINAGE WORKS |  |  |  |  |
| 6 | Providing and fixing on wall face unplasticised- Rigid PVC rain water pipes conforming to IS:13592 type A including jointing with seal ring conforming to IS:5382 leaving 10mm gap for thermal expansion (i) Single socketed pipes – 110mm diameter OD | RM | 100.00 |  |  |
| 7 | Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 (1 cement : 4 coarse sand) and making good the walls etc. complete 110mm | Each | 100.00 |  |  |
| 8 | Providing and fixing to the inlet mouth of rain water pipe cast iron grating 15cm diameter and weighing not less than 440 grams. | Each | 10.00 |  |  |
| 9 | Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion: Bend 87.5°. 110 mm bend | Each | 30.00 |  |  |
|  | TOTAL PART V- CIVIL WORK |  |  |  |  |

| TOTAL PART VI- CIVIL WORK -CONNECTING PASSAGE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SL No | Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| I | SUB HEAD -I - DEMOLISHING ANG DISMANTLING |  |  |  |  |
| 1 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :Of area beyond 3 sq. metres | sqm | 6.30 |  |  |
| 2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement morter | cum | 6.00 |  |  |
| II | SUB HEAD -II - EARTH WORK |  |  |  |  |
| 3 | Earth work in excavation by mechanical means (Hydraulic Excavator )/ manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | cum | 12.00 |  |  |
| 4 | Supplying and providing interlocking sheet piles to the sides of the trenches with interlocking sheet piles supplied, driven down vertically one after another to line and levels with suitable pile driving equipments and accessories up to a maximum depth of 1 m below the bottom of the proposed excavation and extending 50 cm above the ground level suitably with walling pieces with 6 mm thick sheet piles of 4.25 m length installed with M.S channels on 175 mmx90mm RS joist @ 19.3 kg/mt placed and at fastened to the pile wall suitably and struting with wooden joists for hard wood or M.S screw jacks fixed at 2.5 m intervals and maintaining the shoring till the retaining wall is casted and cured and trenches are back filled including conveyance of tools and plants and other materials equipments and all other incidental charges like cleaning of sheet piles and other interlocking arrangements before driving etc dismanting and cleaning restacking for reuse including all abour and hire charges and conveyance of equipments tools and other sundries etc complete | sqm | 15.00 |  |  |
|  | SUB HEAD - III - PLAIN CEMENT CONCRETE |  |  |  |  |
| 5 | Cement concrete(Cast-in-situ) Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering- All work upto plinth level 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40mm nominal size) | cum | 1.00 |  |  |
| III | SUB HEAD - III - REINFORCED CEMENT CONCRETE |  |  |  |  |
| 6 | Providing and laying in position specified grade of reinforced cement concrete including the cost of centering,shuttering,finishing and excluding cost of reinforcment -All work upto plinth level.1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size | cum | 5.00 |  |  |
| 7 | Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) | cum | 5.00 |  |  |
| 8 | Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size) | cum | 12.00 |  |  |
| 9 | Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL) | kg | 3200.00 |  |  |
| IV | SUB HEAD -IV- STEEL WORK |  |  |  |  |
| 10 | Providing and fixing stainless steel ( Grade 304) railing made of Hollow tubes, channels, plates etc. including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in-charge. ( for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc | kg | 300 |  |  |
| V | SUB HEAD -V - FLOORING WORKS |  |  |  |  |
| 11 | Chequered terrazo tiles 22 mm thick with graded marble chips of size up to 6 mm in floors, jointed with neat cement slurry mixed with pigment to match the shade of the tiles including rubbing and polishing complete, on 20 mm thick bed of cement mortar 1:4 (1 cement :4 coarse sand); light shade using white cement | Sqm | 35.00 |  |  |
| VI | SUB HEAD -VI -FINISHING WORKS |  |  |  |  |
| 12 | 15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement :4 fine sand) | Sqm | 100.00 |  |  |
| 13 | 6mm cement plaster to ceiling of mix 1 : 3 (1 cement : 3 fine sand ) | sqm | 30.00 |  |  |
| VII | SUB HEAD -VI - ROOFING WORKS |  |  |  |  |
| 14 | Providing and fixing 15cm wide &45 cm overall semi circular plain GS sheet gutter with iron bracket 40x3 size washers including making nessassary connections with rain water pipe complete. 0.63mm thick zink coating not less than 275kg/m2 | rm | 20 |  |  |
| 15 | Providing and fixing on wall face unplasticised- Rigid PVC rain water pipes conforming to IS:13592 type A including jointing with seal ring conforming to IS:5382 leaving 10mm gap for thermal expansion(i) Single socketed pipes – 110mm diameter OD | RM | 25.00 |  |  |
| 16 | Providing and fixing poly carbonate ( multi wall 6mm or nearest size ) sheet roofing of approved make, colour (blue or gray) and quality fixed with polymer coated J or L hooks ,bolts and nut of required diameter necessary washers complete including the cost of M S square tube 50x25mm 16 guage fixed with M S flat 25x6mm including necessary nuts and bolts to support the roofing , painting with two or more coats with synthetic enamel paint over a priming coat of Zinchromate primer etc complete. with gray coloured sheet. | Sqm | 75 |  |  |
|  | TOTAL PART VI- CIVIL WORK |  |  |  |  |

| ADDITIONAL WORKS AT DISTRICT HOSPITAL AT MANANTHAVADI IN WAYANAD DISTRICT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| TOTAL PART IA –ELECTRICAL WORK- SURGICAL BLOCK |  |  |  |  |  |
| S.No | Item Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| 1 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 Sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required |  |  |  |  |
| a | Group C | Point | 424 |  |  |
| 2 | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5sq.mm. FR PVC insulated copper conductor single core cable etc as required. | Point | 6 |  |  |
| 3 | Power plug wiring in PVC conduit (2x4 sq mm) : Wiring for light/ power plug with 2X4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit along with 1 No 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required | m | 1510 |  |  |
| 4 | Circuit Sub main wiring in PVC Conduit : Wiring for circuit sub main wiring alongwith earthwire with the following sizes of PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. |  |  |  |  |
| a | 2x1.5 sq mm +1x1.5 sq. mm earth wire | m | 2595 |  |  |
| b | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | m | 1950 |  |  |
| c | 4x4 sq mm + 2x4 sq mm earh wire | m | 16 |  |  |
| d | 4x6 sq mm + 2x6 sq mm earh wire | m | 80 |  |  |
| e | 4x10 sq mm + 2x10 sq mm earh wire | m | 10 |  |  |
| 5 | Telephone wiring in existing conduit : Supplying and drawing following pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  |  |
| a | 2 Pair | m | 550 |  |  |
| 6 | T.V. Cable in existing conduit : Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | m | 90 |  |  |
| 7 | S/F PVC conduit : Supplying and fixing of following sizes of medium class PVC conduit along with accessaries in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  |  |
| a | 20 mm | m | 400 |  |  |
| b | 25 mm | m | 150 |  |  |
| 8 | S/F Metal boxes : Supplying and fixing metal box of following sizes ( Nominal size ) on surface or recess with suitable size of phenolic laminated sheet cover in front including painting etc as required. |  |  |  |  |
| a | 200 mm x300 mm x 100 mm deep | Each | 7 |  |  |
| 9 | S/F Modular type switch/ socket : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc as required. |  |  |  |  |
| a | Telephone socket outlet | Each | 30 |  |  |
| b | TV antena socket outlet | Each | 3 |  |  |
| 10 | Supplying and fixing electronic fan regulator : Supplying and fixing stepped type electronic fan regulator on the existing modular plate and switch box excluding modular plate but including connections etc as required. | Each | 95 |  |  |
| 11 | S/F Modular type blanking plates : Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 60 |  |  |
| 12 | S/F Modular boxes, base & cover plate : Supplying and fixing following size/ modules,GI box along with modular base, cover plate for modular switches in recess etc as required. |  |  |  |  |
| a | 1 or 2 module( 75 mmx75 mm) | Each | 35 |  |  |
| 13 | S/F light plug point modular type accessaries : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection,painting etc as required, (For light plugs to be used in non residential buildings }. | Each | 216 |  |  |
| 14 | S/F Power plug point with modular type switch : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each | 70 |  |  |
| 15 | S/F Ceiling rose : Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each | 250 |  |  |
| 16 | ITC Fluroscent fitting directly on surface : Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FR PVC insulated,copper conductor, single core cable and earthing etc as required. | Each | 185 |  |  |
| 17 | ITC Fluroscent fitting with down rod : Installation and testing commissioning of prewired, fluorescent fitting/compact fluorescent fitting of all types, complete with all accessories and tube etc, including supplying and fixing ball and socket arrangement, 2 Nos down rods of 20 mm dia x 1.6 mm thick steel conduit up to 30 cm length, painting and wiring the down rods and connection with 1.5 sq mm FR PVC insulated, copper conductor single core cable and earthing etc as required. | Each | 8 |  |  |
| 18 | S/F extra down rod : Providing and fixing extra conduit down rod of 20 mm dia, 2 x 10 cm length wiring with2 x 1.5 sq mm FR PVC insulated, copper conductor, single core cable including painting etc as required. ( Note: More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 10 |  |  |
| 19 | ITC Ceiling fan : Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length { Up to 30 Cm } with 1.5 sq mm FR PVC insulated, copper conductor, single core cable as required. | Each | 95 |  |  |
| 20 | Extra down rod 15 mm dia : Supplying and fixing extra down rod of 10 Cm length G. I pipe, 15 mm dia, heavy guage including painting etc. as required ( Note: More than 5 Cm length shall be rounded to the nearest 10 Cm and 5 Cm or less shall be ignored) | Each | 50 |  |  |
| 21 | ITC Exhaust fan up to 450 mm sweep: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | Each | 28 |  |  |
| 22 | S/F TPMCB DB : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  |  |
| a | 4 way ( 4+12 ), Double door | Each | 6 |  |  |
| b | 6 way ( 4+18 ), Double door | Each | 5 |  |  |
| 23 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer) as required. |  |  |  |  |
| a | 4 way (4 + 12), Double door | Each | 4 |  |  |
| b | 8 way (4 + 24), Double door | Each | 1 |  |  |
| 24 | S/F 'C' series, MCB : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |
| a | Single pole | Each | 130 |  |  |
| b | Triple Pole | Each | 10 |  |  |
| 25 | S/F SP MCB blanking plate : Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 50 |  |  |
| 26 | S/F FP MCB isolator : Supplying and fixing following rating, four pole,415 Volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |
| a | 40 amps | Each | 7 |  |  |
| b | 63 amps | Each | 6 |  |  |
| c | 100 amps | Each | 3 |  |  |
| 27 | S/F FP RCCB : Supplying and fixing following rating, four pole, 415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |
| a | 25 amps | Each | 7 |  |  |
| b | 40 amps | Each | 5 |  |  |
| c | 63 Amps | Each | 4 |  |  |
| 28 | S/F 20A SPN MCB industrial socket outlet : Supplying and fixing 20 amps, 240 Volts, SPN industril type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps 'C' series, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | Each | 18 |  |  |
| 29 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each | 4 |  |  |
| 30 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Each | 4 |  |  |
| 31 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | m | 30 |  |  |
| 32 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required | m | 120 |  |  |
| 33 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. |  |  |  |  |
| a | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 360 |  |  |
| b | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | m | 30 |  |  |
| 34 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  |  |
| a | 3.5 C x 150 sqmm | Each | 2 |  |  |
| b | 3.5 C x 35 sqmm | Each | 2 |  |  |
| c | 4 C x 25 sqmm | Each | 10 |  |  |
| d | 4 C x 16 sqmm | Each | 8 |  |  |
| e | 4 C x 10 sqmm | Each | 4 |  |  |
| 35 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date. |  |  |  |  |
| a | 3.5 C x 150 sqmm | m | 30 |  |  |
| b | 3.5 C x 35 sqmm | m | 25 |  |  |
| c | 4 C x 25 sqmm | m | 150 |  |  |
| d | 4 C x 16 sqmm | m | 140 |  |  |
| e | 4 C x 10 sqmm | m | 50 |  |  |
| 36 | Supplying and laying 8 SWG copper wire in ground / wall surface for conductor earth electrode, including soldering etc as required | m | 60 |  |  |
| 37 | Supplying and laying/fixing 10 SWG copper wire along with MV cales in ground/wall surface for conductor earth electrode, including soldering etc as required | m | 670 |  |  |
| 38 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 63amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each | 6 |  |  |
| 39 | Supply of 1x28W fluorescent tube light fitting with powder coated CRCA sheet channel complete with all accessories, electronic ballast, lamp holder, 28W lamp etc as required. (Philips TMS540 HF / Crompton T5JB 1328EB / GE LMS 28 N N) | Each | 185 |  |  |
| 40 | Supply and fixing of 3x36W, indoor clean room, recess mounted fluorescent light fixture with CRCA housing, reflector and control gear tray duly powder coated, clear acrylic diffuser, non-hygroscopic gasket to ensure dust proofing, lamp, ballast, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (Philips FBS650 3XPL-L36W EBP ROP / Crompton CRFW12336EB / GE CRP 424FTL BO) | Each | 18 |  |  |
| 41 | Supply and of 2x28 W surface mounted mirror optic luminarie suitable for linear fluroscent lamp TL 5- 28 W lamp with all accessories like ballast, lamp, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (TCS 350 2xTL5-28W EBE CS / Crompton T5CS228EB / GE GETC 2x28 MOS HF) | Each | 8 |  |  |
| 42 | Supply & fixing 2x18W recess mounted closed downlight luminarie with centre frosted glass cover suitable for horizondal lamp complete with all accessories, electronic ballast, lamp holder, 18W lamp etc as required. ( Philips FBS085 2xPL-C/4P18W HFB RG-FR / Crompton DDLHR218EB/G/SL / GE CFL C 2x18 DN FG LH R (H) HF) | Each | 25 |  |  |
| 43 | Supply & fixing of 2x28W Indoor Decorative recessed mirror optics luminarie complete with all accessories like suitable TL5- 28w lamps, suitable ballast, chains, hooks etc. ( TBS520 2XTL5-28W MI EBE / Crompton T5CR228EB) | Each | 16 |  |  |
| 44 | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod, suspension shackle, canopy etc. (Make: Usha Technix flair star rated or equi). | Each | 95 |  |  |
| 45 | Supply of 250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/ shutters and all accessories as required complete. (Make : Usha Crisp Air or Equi) | Each | 26 |  |  |
| 46 | Supply of 450mm sweep, 1400 rpm, heavy duty exhaust fan suitable for single phase 230 volt, 50Hz AC supply complete with all accessories as required. (Make : Usha heavy duty turbo or equi) | Each | 2 |  |  |
| 47 | Supply and fixing 400 mm sweep wall fan, swinging type with speed control and necessary adapter, of approved quality and colour. (Make : Usha - Maxx Air or equi) | Each | 10 |  |  |
| 48 | Supplying and fixing 1x36W CFL Decorative compact street light luminaire with sheet steel aluminium housing, UV stabilized acrylic cover, lamp etc complete with all mounting accessories as required. The item shall also include suitable size bracket fabricated out of B class G.I pipe to suit the fitting with its clamping accessories as required. (Philips FGS 120 1XPL-L36W HF / Crompton SCE 1336) | Each | 8 |  |  |
| 49 | Supplying and fixing ISI marked PVC batten/ angle holder including 15 watt ISI marked CFL lamp, connections etc. as required. | Each | 95 |  |  |
| 50 | Supply and installation of 10 telephone terminal box with 10 pair Krone module including all mounting accessories as required. | Each | 3 |  |  |
| 51 | Supply, Installation, Testing & Commissioning of LT panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification. |  |  |  |  |
|  | Incomer |  |  |  |  |
|  | 1 no. 315A, 35kA, TP+NL MCCB having isolation duty with E/F rlease, adjustable thermal magnetic release for O/L & SC protection. |  |  |  |  |
|  | 1 no. 315A, 35kA, FP, ATS (Automatic change over Switch) with thermal magnetic release, voltage and frequency display, inbuilt UV and phase unbalance protection. The ATS should have the facility for automatic and manual control. |  |  |  |  |
|  | The ATS is used for the automatic operation of the DG set. The item shall include all necessary accessories, control cabling from the DG set to the panel / ATS. |  |  |  |  |
|  | BusBar |  |  |  |  |
|  | 1 Set of 400A TPN busbars of high conductivity electrolytic quality Aluminium alloy. |  |  |  |  |
|  | 1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing. |  |  |  |  |
|  | Instruments |  |  |  |  |
|  | 1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1. |  |  |  |  |
|  | 1 Set of phase indicating lamps, LED type, RYB. |  |  |  |  |
|  | 1 Set of 2A 10kA C curve SP control MCB |  |  |  |  |
|  | 1 Set of 400/5A, Class 1.0, 10VA, Cast Resin CT |  |  |  |  |
|  | OutGoings |  |  |  |  |
|  | 1no 200A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load. |  |  |  |  |
|  | 6 nos. 63A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load. |  |  |  |  |
|  | 4 nos. 32A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.. | Each | 1 |  |  |
| 52 | Supply, Installation, Testing & Commissioning of Second floor LT panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification. |  |  |  |  |
|  | Incomer |  |  |  |  |
|  | 1no 200A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load. |  |  |  |  |
|  | BusBar |  |  |  |  |
|  | 1 Set of 250A TPN busbars of high conductivity electrolytic quality Aluminium alloy. |  |  |  |  |
|  | 1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing. |  |  |  |  |
|  | Instruments |  |  |  |  |
|  | 1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1. |  |  |  |  |
|  | 1 Set of phase indicating lamps, LED type, RYB. |  |  |  |  |
|  | 1 Set of 2A 10kA C curve SP control MCB |  |  |  |  |
|  | 1 Set of 200/5A, Class 1.0, 10VA, Cast Resin CT |  |  |  |  |
|  | OutGoings |  |  |  |  |
|  | 8 nos. 63A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load. |  |  |  |  |
|  | 6 nos. 32A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.. | Each | 1 |  |  |
| 53 | Supply and providing 6 mm thick & 1 m wide electrical grade chequered type rubber mat to withstand 3.3 KV dielectric strength conforming to IS 5429/ 1969. | m | 10 |  |  |
|  | TOTAL PART IA –ELECTRICAL WORK |  |  |  |  |

| MANANTHAVADY HOSPITAL- MATERNITY BLOCK ABSTRACT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| TOTAL PART IIA –ELECTRICAL WORK -MATERNITY BLOCK |  |  |  |  |  |
| SL. No | Item Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| 1 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5Sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required |  |  |  |  |
| a | Group C | Point | 20 |  |  |
| 2 | Power plug wiring in PVC conduit (2x4 sq mm) : Wiring for light/ power plug with 2X4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit along with 1 No 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required | m | 200 |  |  |
| 3 | Circuit Sub main wiring in PVC Conduit : Wiring for circuit sub main wiring alongwith earthwire with the following sizes of PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. |  |  |  |  |
| a | 2x1.5 sq mm +1x1.5 sq. mm earth wire | m | 80 |  |  |
| b | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | m | 165 |  |  |
| c | 4x4 sq mm + 2x4 sq mm earh wire | m | 20 |  |  |
| 4 | Supplying and drawing 2 pair 0.5 sqmm FR PVC insulated annealed copper conductor, unarmoured telephone cable in the existing surface / recessed steel / PVC conduit as required. | m | 40 |  |  |
| 5 | Supply and fixing 20mm medium class PVC conduit along with accessories in surface / recess including cutting the wall and making good the same in case of recessed conduit as required. | m | 40 |  |  |
| 6 | Supply and fixing modular type telephone outlet in modular type GI box along with modular base and cover plate including connection in surface / recess etc as required. | Each | 2 |  |  |
| 7 | S/F Modular type blanking plates : Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 18 |  |  |
| 8 | S/F light plug point modular type accessaries : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection,painting etc as required, (For light plugs to be used in non residential buildings }. | Each | 12 |  |  |
| 9 | S/F Power plug point with modular type switch : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each | 11 |  |  |
| 10 | S/F Ceiling rose : Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each | 9 |  |  |
| 11 | ITC Fluroscent fitting directly on surface : Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FR PVC insulated,copper conductor, single core cable and earthing etc as required. | Each | 4 |  |  |
| 12 | ITC Exhaust fan up to 450 mm sweep: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | Each | 1 |  |  |
| 13 | S/F TPMCB DB : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  |  |
| a | 4 way ( 4+12 ), Double door | Each | 1 |  |  |
| 14 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer) as required. |  |  |  |  |
| a | 4 way (4 + 12), Double door | Each | 1 |  |  |
| 15 | S/F 'C' series, MCB : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |
| a | Single pole | Each | 8 |  |  |
| b | Triple Pole | Each | 6 |  |  |
| 16 | S/F SP MCB blanking plate : Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 10 |  |  |
| 17 | S/F FP MCB isolator : Supplying and fixing following rating, four pole,415 Volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |
| a | 40 amps | Each | 1 |  |  |
| b | 63 amps | Each | 1 |  |  |
| 18 | S/F FP RCCB : Supplying and fixing following rating, four pole, 415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |
| a | 25 amps | Each | 1 |  |  |
| c | 63 Amps | Each | 1 |  |  |
| 19 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each | 3 |  |  |
| 20 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required | m | 40 |  |  |
| 21 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  |  |
| a | Above 95 sq. mm and upto 185 sq. mm | m | 50 |  |  |
| 22 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. |  |  |  |  |
| a | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 125 |  |  |
| b | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | m | 30 |  |  |
| 23 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  |  |
| a | 3.5 C x 150 sqmm | Each | 2 |  |  |
| b | 4 C x 16 sqmm | Each | 4 |  |  |
| c | 4 C x 25 sqmm | Each | 2 |  |  |
| 24 | Providing, laying and fixing of 100mm dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required | m | 6 |  |  |
| 25 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date. |  |  |  |  |
| a | 3.5 C x 150 sqmm | m | 80 |  |  |
| b | 4 C x 16 sqmm | m | 100 |  |  |
| c | 4 C x 25 sqmm | m | 25 |  |  |
| 26 | Supplying and laying 8 SWG copper wire at 0.50 metre below ground level for conductor earth electrode, including soldering etc as required | m | 160 |  |  |
| 27 | Supplying and laying/fixing 12 SWG copper wire along with MV cables in ground/wall surface for conductor earth electrode, including soldering etc as required | m | 180 |  |  |
| 28 | Supply of 1x28W fluorescent tube light fitting with powder coated CRCA sheet channel complete with all accessories, electronic ballast, lamp holder, 28W lamp etc as required. (Philips TMS540 HF / Crompton T5JB 1328EB / GE LMS 28 N N) | Each | 4 |  |  |
| 29 | Supply and fixing of 3x36W, indoor clean room, recess mounted fluorescent light fixture with CRCA housing, reflector and control gear tray duly powder coated, clear acrylic diffuser, non-hygroscopic gasket to ensure dust proofing, lamp, ballast, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (Philips FBS650 3XPL-L36W EBP ROP / Crompton CRFW12336EB / GE CRP 424FTL BO) | Each | 4 |  |  |
| 30 | Supply of 250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/ shutters and all accessories as required complete. (Make : Usha Crisp Air or Equi) | Each | 1 |  |  |
| 31 | Supply & fixing 2x18W recess mounted closed downlight luminarie with centre frosted glass cover suitable for horizondal lamp complete with all accessories, electronic ballast, lamp holder, 18W lamp etc as required. ( Philips FBS085 2xPL-C/4P18W HFB RG-FR / Crompton DDLHR218EB/G/SL / GE CFL C 2x18 DN FG LH R (H) HF) | Each | 5 |  |  |
| 32 | Supplying and fixing ISI marked PVC batten/ angle holder including 15 watt ISI marked CFL lamp, connections etc. as required. | Each | 5 |  |  |
| 33 | Dismantling the existing wiring with switch box, switch, socket (6&16A) and stacking the same to the place as per the direction of engineer in charge. | Each | 19 |  |  |
| 34 | Dismantling the existing all types of light fixing, ceiling fan, exhaust fan, wall fan etc. and stacking the same to the place as per the direction of engineer in charge. | Each | 6 |  |  |
| 35 | Supply, Installation, Testing & Commissioning of LT panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification. |  |  |  |  |
|  | Incomer |  |  |  |  |
|  | 1 no. 200A, 25kA, TP+NL MCCB having isolation duty with E/F rlease, adjustable thermal magnetic release for O/L & SC protection. |  |  |  |  |
|  | 1 no. 200A, FP, On-load changeover switch with extended rotory handle. |  |  |  |  |
|  | BusBar |  |  |  |  |
|  | 1 Set of 250A TPN busbars of high conductivity electrolytic quality Aluminium alloy. |  |  |  |  |
|  | 1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing. |  |  |  |  |
|  | Instruments |  |  |  |  |
|  | 1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1. |  |  |  |  |
|  | 1 Set of phase indicating lamps, LED type, RYB. |  |  |  |  |
|  | 1 Set of 2A 10kA C curve SP control MCB |  |  |  |  |
|  | 1 Set of 200/5A, Class 1.0, 10VA, Cast Resin CT |  |  |  |  |
|  | OutGoings |  |  |  |  |
|  | 1no 125A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load. |  |  |  |  |
|  | 5 nos. 63A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load. |  |  |  |  |
|  | 2 nos. 32A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.. | Each | 1 |  |  |
| 36 | Supply and providing 6 mm thick & 1 m wide electrical grade chequered type rubber mat to withstand 3.3 KV dielectric strength conforming to IS 5429/ 1969. | m | 5 |  |  |
| 37 | Supplying and fixing TP sheet steel enclosure on surface / recess along with 63A, 415 Volts, "C" series, TP miniature circuit breaker complete with connections, testing and commissioning etc as required. | Each | 3 |  |  |
|  | TOTAL PART IIA –ELECTRICAL WORK |  |  |  |  |

| MANANTHAVADY HOSPITAL- OP BLOCK ABSTRACT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| TOTAL PART IIIA –ELECTRICAL WORK - KHRWS PAYWARD |  |  |  |  |  |
|  | Item Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
|  | COPPER WIRING IN PVC CONDUIT. |  |  |  |  |
| 1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5Sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required | Point | 10 |  |  |
| 2 | Wiring for circuit sub main wiring alongwith earthwire with the following sizes of PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. |  |  |  |  |
| a | 2x1.5 sq mm +1x1.5 sq. mm earth wire | m | 60 |  |  |
| b | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | m | 20 |  |  |
| c | 2x4 sq mm + 1x4 sq mm earh wire | m | 15 |  |  |
| 3 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection, painting etc as required, | Each | 8 |  |  |
| 4 | Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each | 10 |  |  |
| 5 | Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FR PVC insulated,copper conductor, single core cable and earthing etc as required. | Each | 10 |  |  |
| 6 | Supply of 1x28W fluorescent tube light fitting with powder coated CRCA sheet channel complete with all accessories, electronic ballast, lamp holder, 28W lamp etc as required. (Philips TMS540 HF / Crompton T5JB 1328EB / GE LMS 28 N N) | Each | 10 |  |  |
| 7 | Dismantling the existing wiring with switch box, switch, socket (6&16A) and stacking the same to the place as per the direction of engineer in charge. | Each | 4 |  |  |
| 8 | Dismantling the existing all types of light fixing, ceiling fan, exhaust fan, wall fan etc. and stacking the same to the place as per the direction of engineer in charge. | Each | 10 |  |  |
|  | TOTAL PART IIIA –ELECTRICAL WORK |  |  |  |  |

| MANANTHAVADY HOSPITAL- DG ABSTRACT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| TOTAL PART IVA –ELECTRICAL WORK -DG-SET |  |  |  |  |  |
| SL. No | Item Description | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| 1 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Each | 2 |  |  |
| 2 | Earthing with Copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Each | 2 |  |  |
| 3 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | m | 20 |  |  |
| 4 | Supplying and laying 25 mm X 5 mm GI strip at 0.50 metre below ground as strip earth electrode, including connection/terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of GI nut bolt & spring washer spaced at 50mm) | m | 35 |  |  |
| 5 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | m | 20 |  |  |
| 6 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | m | 65 |  |  |
| 7 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required |  |  |  |  |
| a | Above 95 sq. mm and upto 185 sq. mm | m | 30 |  |  |
| 8 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. |  |  |  |  |
|  | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | m | 30 |  |  |
| 9 | Supplying and making indoor end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  |  |
|  | 3½ X 185 sq. mm (57mm) | Each | 4 |  |  |
| 10 | Providing, laying and fixing 100mm dia GI pipe (medium class) in ground complete with GI fittings including trenching (75cm deep) and refilling etc as required. | m | 20 |  |  |
| 11 | Supply, Installation, Testing and Commissioning of 160 KVA, silent type, water cooled, radiator type, four stroke, electric start D.G Set with acoustic enclosure and standard control panel with 250A, TPN, thermal magnetic MCCB, ammeter, voltmeter, energy meter, frequency meter, indication lamp etc. The engine shall be capable of taking 10% overload for one hour after 12 hours of continuous operation. The DG shall be suitable for AMF operation. The alternator shall be brushless, self excited, self regulated, SPDP enclosure, class F/H insulation, suitable for continuous operation at 1500 rpm, generating 415 V +/- 5% at 0.8 p.f, 50Hz, 0.85 load factor, 3 phase, 4 wire system generally conforming to BS: 2613 & IS: 4722. The neutral of the DG set shall be provided with low set earth fault relay using 50/5A 5P10 10VA CT in the neutral earthing conductor . |  |  |  |  |
|  | Both Engine and Alternator shall be mounted on common channel iron base frame, and with standard accessories such as antiviberation pad, lead acid batteries (as specified by engine manufacturer) and engine driven battery charger along with leads, battery stand, fuel piping from fuel tank to Engine, electronic governor, Residential silencer, suitable size cable termination box etc as required. Rate shall be inclusive of all lift, lead charges. The work should be as per Electrical Inspectorate / Pollution control board norms. | Job | 1 |  |  |
| 12 | Supply & installation of exhaust gas piping of suitable diameter for 160 kVA DG set as per manufactures standard welded black MS, B class pipe confirming to IS:3589 cut to required lengths and installed with necessary bends, supports and clamps, anti- vibration mountings, insulation of exhaust system with mineral wool / Rockwool, 50mm thick wire mesh & aluminum cladding etc as required. | m | 20 |  |  |
| 13 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date. |  |  |  |  |
|  | 3.5 C x 185 sqmm | m | 60 |  |  |
| 14 | Supplying and laying 8 SWG copper wire at 0.50 metre below ground level for conductor earth electrode, including soldering etc as required | m | 120 |  |  |
| 15 | Preparation of schematic drawing and getting approval from Electrical inspectorate, Kerala State Electricity Board, PCB and any statutory bodies, including all liaison works etc complete as required. (The fees paid will be reimbursed by the client on production of original receipts). | Job | 1 |  |  |
|  | TOTAL PART IVA –DG SET |  |  |  |  |

| TOTAL PART VA - SITC OF FIRE ALARM SYSTEM FOR VANITHA TRIBAL MATERNITY WARD 80 BEDDED HOSPITAL MANANTHAVADY |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SL NO | DESCRIPTION | QTY | UNIT | Rate(in Words and Figures) | Amount (in Words and Figures) |
| 1 | EXTINGUISHER |  |  |  |  |
|  | Supply and installation of DCP type fire extinguisher of 5 kg. Capacity complete with initial charges and installation brackets.Supply and installation, testing and commissioning of DCP type fire extinguisher with 5 kg. Capacity complete with installation brackets with ISI mark IS:2171/13849 | 12 | No |  |  |
| 2 | Supply and installation, testing and commissioning of CO2 type fire extinguisher with 4.5 kg. Capacity complete with installation brackets with ISI mark IS:2878 | 3 | No |  |  |
| 3 | ADDRESSABLE FIRE ALARM PANEL |  |  |  |  |
|  | Supply, installation, testing & commissioning of networkable Two Loop Micro processor based 2 wire fault tolerant loop with optional redunadant network module, each loop shall have the cpability of connecting 125 devices.The fire alarm control panel shall have built in degarde mode function.The panel should have inbuilt TCP/IP communication for Panel Program and Remote Monitoring option through LAN or WAN communication.The panel shall be able to give location of all fire and More Fire /fault and Isolation conditions of addressable units via the address codes.The panel shall have the capacity of storing upto 2000 events.Further, the panel must be able to automatically switch ON /OFF respective control module when ever any alarm is triggered. The panel should have inbuilt common Alarm, Fault and monitored sounder output. The panel shall have a 8x40 characters LCD display with resolution of 256 X 112 pixels, and analog output, external/inbuilt printer to log all fire or fault events complete in all respects. The Panel Should have protection caregory of IP30. Also the panel should have the option to operate in manned and unmanned mode.The Panel Shall have the option of 24/48/96 Zones with Individual LED Indicators or with in the Loop mimic driver for 96 LED indicators.The panel shall have a built in power supply and battery charger along with maintenance free 24 AH, 2 x 12 volt SMF Lead acid batteries capable of running for a minimum of 24 hours with battery charger complete as required.and as per specifications and Duly Approved by EN54/LPCB/VDS/FM | 1 | NO |  |  |
| 4 | SMOKE DETECTORS |  |  |  |  |
|  | Supply and installation, testing and commissioning , of Intelligent Analog Addressable Multi-Sensor type Smoke Detector with inbuilt turbo Isolator and integral response indicator with 360 degree viewing angle. Detector shall communicate 3 danger levels for differentiated alarm activation and high tolerance to dust,dirt, temperature fluctuations and air currents. Detector should have unquie address for communication and assigned through panel with Mounting Base as required with the protection category of IP40 and Duly Approved by EN54/LPCB/VDS/FM/UL | 88 | No |  |  |
| 5 | HEAT DETECTORS |  |  |  |  |
|  | Supply and installation, testing and commissioning of Intelligent Analog Addressable Heat Detector (Static + ROR) with inbuilt turbo Isolator and integral response indicator with 360 degree viewing angle. Detector shall communicate 3 danger levels for differentiated alarm activation. Detector should have unquie address for communication and assigned through panel with Mounting Base as required with the protection category of IP40 and Duly Approved by EN54/LPCB/VDS/FM/UL | 6 | No |  |  |
| 6 | MANUAL CALL POINT |  |  |  |  |
|  | Supply and installation, testing and commissioning of of Inteliigent addressable manual call point with inbuilt turbo Isolator suitable for flush or surface mounting, call point shall include test key feature without removing the glass. Also should have protection category of IP44 and extra acceesories as required, duly approved by EN54/LPCB/VDS/FM | 6 | No |  |  |
| 7 | LOOP POWERED SOUNDER |  |  |  |  |
|  | Supply and installation, testing and commissioning of Inteliigent addressable loop powered sounder/external power sounder with base, inbuilt turbo Isolator, able to provide an o/p of 90dBA at 1m, peak light o/p of at least 3.2cd and shall have 11 programmable tones, 3 volume settings selectable from the panel and fully synchronized with other sounders and shall have the ability to switch between one tone for alert and one tone for evacuation. Shall have protection category of IP42 and duly approved by EN54/LPCB/VDS/FM | 6 | No |  |  |
| 8 | INPUT MODULE |  |  |  |  |
|  | Supply and installation, testing and commissioning of Addressable four input/out put module with inbuilt isolator and shall have the LED indication for Normal, Fault, test, and activation.The module shall have the option for configuration as fail safe operation and duly approved by EN54/LPCB/VDS/FM | 2 | No |  |  |
| 9 | FRLS CABLE |  |  |  |  |
|  | Supplyand installation, testing and commissioning of 2C x 1.5 Sq.mm twisted pair copper cable ISI marked with proper clamping, supports and terminations.. | 1020 | Mtr |  |  |
|  | TOTAL PART VA |  |  |  |  |

| TOTAL PART V B SITC OF FIRE ALARM SYSTEM FOR SURGICAL COMPLEX, MANANTHAVADY |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SL NO | DESCRIPTION | QTY | UNIT | Rate(in Words and Figures) | Amount (in Words and Figures) |
| 1 | EXTINGUISHER |  |  |  |  |
|  | Supply and installation of DCP type fire extinguisher of 5 kg. Capacity complete with initial charges and installation brackets.Supply and installation, testing and commissioning of DCP type fire extinguisher with 5 kg. Capacity complete with installation brackets with ISI mark IS:2171/13849 | 9 | No |  |  |
| 2 | Supply and installation, testing and commissioning of CO2 type fire extinguisher with 4.5 kg. Capacity complete with installation brackets with ISI mark IS:2878 | 3 | No |  |  |
| 3 | ADDRESSABLE FIRE ALARM PANEL |  |  |  |  |
|  | Supply, installation, testing & commissioning of networkable Two Loop Micro processor based 2 wire fault tolerant loop with optional redunadant network module, each loop shall have the cpability of connecting 125 devices.The fire alarm control panel shall have built in degarde mode function.The panel should have inbuilt TCP/IP communication for Panel Program and Remote Monitoring option through LAN or WAN communication.The panel shall be able to give location of all fire and More Fire /fault and Isolation conditions of addressable units via the address codes.The panel shall have the capacity of storing upto 2000 events.Further, the panel must be able to automatically switch ON /OFF respective control module when ever any alarm is triggered. The panel should have inbuilt common Alarm, Fault and monitored sounder output. The panel shall have a 8x40 characters LCD display with resolution of 256 X 112 pixels, and analog output, external/inbuilt printer to log all fire or fault events complete in all respects.The Panel Should have protection caregory of IP30. Also the panel should have the option to operate in manned and unmanned mode.The Panel Shall have the option of 24/48/96 Zones with Individual LED Indicators or with in the Loop mimic driver for 96 LED indicators.The panel shall have a built in power supply and battery charger along with maintenance free 24 AH, 2 x 12 volt SMF Lead acid batteries capable of running for a minimum of 24 hours with battery charger complete as required.and as per specifications and Duly Approved by EN54/LPCB/VDS/FM | 1 | NO |  |  |
| 4 | SMOKE DETECTORS |  |  |  |  |
|  | Supply and installation, testing and commissioning , of Intelligent Analog Addressable Multi-Sensor type Smoke Detector with inbuilt turbo Isolator and integral response indicator with 360 degree viewing angle. Detector shall communicate 3 danger levels for differentiated alarm activation and high tolerance to dust,dirt, temperature fluctuations and air currents. Detector should have unquie address for communication and assigned through panel with Mounting Base as required with the protection category of IP40 and Duly Approved by EN54/LPCB/VDS/FM/UL | 114 | No |  |  |
| 5 | HEAT DETECTORS |  |  |  |  |
|  | Supply and installation, testing and commissioning of Intelligent Analog Addressable Heat Detector (Static + ROR) with inbuilt turbo Isolator and integral response indicator with 360 degree viewing angle. Detector shall communicate 3 danger levels for differentiated alarm activation. Detector should have unquie address for communication and assigned through panel with Mounting Base as required with the protection category of IP40 and Duly Approved by EN54/LPCB/VDS/FM/UL | 4 | No |  |  |
| 6 | MANUAL CALL POINT |  |  |  |  |
|  | Supply and installation, testing and commissioning of of Inteliigent addressable manual call point with inbuilt turbo Isolator suitable for flush or surface mounting, call point shall include test key feature without removing the glass. Also should have protection category of IP44 and extra acceesories as required, duly approved by EN54/LPCB/VDS/FM | 3 | No |  |  |
| 7 | LOOP POWERED SOUNDER |  |  |  |  |
|  | Supply and installation, testing and commissioning of Inteliigent addressable loop powered sounder/external power sounder with base, inbuilt turbo Isolator, able to provide an o/p of 90dBA at 1m, peak light o/p of at least 3.2cd and shall have 11 programmable tones, 3 volume settings selectable from the panel and fully synchronized with other sounders and shall have the ability to switch between one tone for alert and one tone for evacuation. Shall have protection category of IP42 and duly approved by EN54/LPCB/VDS/FM | 3 | No |  |  |
| 8 | INPUT MODULE |  |  |  |  |
|  | Supply and installation, testing and commissioning of Addressable four input/out put module with inbuilt isolator and shall have the LED indication for Normal, Fault, test, and activation.The module shall have the option for configuration as fail safe operation and duly approved by EN54/LPCB/VDS/FM | 2 | No |  |  |
| 9 | FRLS CABLE |  |  |  |  |
|  | Supplyand installation, testing and commissioning of 2C x 1.5 Sq.mm twisted pair copper cable ISI marked with proper clamping, supports and terminations.. | 1085 | Mtr |  |  |
|  | TOTAL PART V B |  |  |  |  |

| TOTAL PART VI A Air Conditioning Works - Vanitha Tribal Maternity Ward 80 bedded Hospital |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item |  | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| No. | Description of items |  |  |  |  |
| PART A | MACHINERY |  |  |  |  |
| 1 | Supply, intallation, testing and commissioning (SITC) of 5.5 TR capacity aircooled Outdoor condensing unit with scroll compressor as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, hermetically sealed scroll compressor, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, high-low pressure cut out, suitable for three phase 440V supply. | No | 1 |  |  |
| 2 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 5.5TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition |  |  |  |  |
| a | Suction Line | RM | 11 |  |  |
| b | Liquid Line | RM | 11 |  |  |
| 3 | SITC of DX type double skinned air handling units,ceiling suspended/floor mounting type 5.5 TR, 1000 lps capcity complete with suitable DIDW blower (asper approved make), blower section, static pressure of 80mm of water column, built in pre filter(EU4), fine filter(EU7) and controls connected to condensing units, insulated SS drain pan, 6 row cooling coil, electric motor, belt drive package with TEFC motor class 'B' insulation, suitable for 3 phase, 415 V, 50Hz supply, suitable AHU panel, ARI certified, belt guards, with 0.6mm double skinned 40mm thick PUF panel, suitable supports for suspending from slab, vibration isolator, etc. conforming to specifications. The air handling units shall have 1 inlet refrigerant coils and 1 outlet refrigerant coils suitable for 1 numbers of 5.5 TR capacity ODU and shall conform to specifications. | No | 1 |  |  |
| 4 | Supply, installation, testing and commissioning of Air Cooled High Wall mounted Split Air Conditioner of following capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, standard 5 m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 5m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit, ODU MS stand, first charge refrigarant gas, suitable stabilizer etc complete as required. |  |  |  |  |
| 4.1 | 1.5 TR 5 star rated as per BEE | Each | 2 |  |  |
| 5 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping with 13 mm nitrile rubber insulation and electrical connection interconnecting the condensing unit to evaporating unit for split AC's as per site condition | RM | 14 |  |  |
| 6 | Supply, Laying and Fixing of control wiring of suitable size required from the Indoor to outdoor units for all units as per specification. | RM | 7 |  |  |
| 7 | Supply, installation, testing and commissioning PVC drain pipe of 25mm dia ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification | RM | 13 |  |  |
| 8 | SITC of Humidity Controller electric strip heaters in supply air plenum complete with fixing arrangements, thermostats and safety thermostat including all power and control wiring | No | 1 |  |  |
| PART B | AIR DISTRIBUTION |  |  |  |  |
| 9 | Supply, installation, testing and commissioning of factory fabricated rectangular Aluminum sheet metal ducting for Supply/return/fresh air duct/collar connecting to indoor unit as per ducting specifications and with suitable supports using MS angles, channels, rods, anchor bolts, etc to roof /truss as per IS 655 and as per specifications. |  |  |  |  |
| 9.1 | 20 G | SQM | 9 |  |  |
| 9.2 | 22 G | SQM | 71 |  |  |
| 10 | Supply, installation, testing and commissioning of factory fabricated rectangular GSS sheet metal ducting for Supply/return/fresh air duct/collar connecting to indoor unit as per ducting specifications and with suitable supports using MS angles, channels, rods, anchor bolts, etc to roof /truss as per IS 655 and as per specifications. |  |  |  |  |
| 10.1 | 22 G | SQM | 5 |  |  |
| 10.2 | 24 G | SQM | 16 |  |  |
| 11 | SITC of External thermal insulation on supply air ducts using min 13mm thick nitrile rubber class "O" closed cell type with antimicrobial protection as per specifications | SQM | 80 |  |  |
| 12 | Supply, installation, testing and commissioning of Acoustic duct lining using 10mm nitrile rubber insulation open cell type inside the ducts, antimicrobial protection at the outlets of all indoor units upto 4m distance from fan outlet as per spec provided. | SQM | 16 |  |  |
| 13 | Supply, installation and comissioning of underdeck insulation with 20 mm thick closed cell elastomeric Nitrile Rubber density of 40kg/m3 on ceiling with necessary adhesive, 600X600mm GI netting, fixtures, supports etc. | SQM | 7 |  |  |
| 14 | Supply, fabrication, installation, testing of flexible connections made out of fire resistant flexible double canvas sleeve. | Set | 1 |  |  |
| 15 | Supply, installation, testing and comissioning of Powder coated extruded aluminimum Continuous grilles 16mm frame, as per spec | SQM | 3 |  |  |
| 16 | SITC of Fire Control Damper made of 16G GSS sheet blade and frame with 165mm casing, heavy duty interlocking blades and fuly enclosed bade linkage mechanism, SS lateral seal blade seals, self lubricating sintered bronze bushes, fire rating as per UL555-1995 tested as per BS-476 part 20 with 18G extended sleeve 450mm and with fusible link, spring mechanism control panel temp sensor, smoke sensor, limit swith with lever for auto shut off in case of fire/smoke as per specifications. | SQM | 1 |  |  |
| 17 | SITC of multi blade type volume control dampers made of extruded auminium for ducts/ collars to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distributions system in main ducts, return ducts & other area as per specification. | SQM | 2 |  |  |
| 18 | SITC of Fresh air GI louvers of size 300x300 mm with wire mesh and birds screen for IDUs/AHUs as per specifications. | SQM | 1 |  |  |
| 19 | Supply and fixing of Terminal HEPA Filters having filtering efficiency of 99.7% down to 0.3 microns with aluminum frame works, suitable for fixing in the Supply air plenum boxes |  |  |  |  |
| 19.1 | 610 x 610 x305 | Nos | 4 |  |  |
| 19.2 | 450 x 450 x305 | Nos | 1 |  |  |
| 20 | SITC of Plenum box made of 18G Aluminum sheet with frame work for fixing HEPA filters at terminalsand provision of access door for removing the HEPA Filters for cleaning and replcaement .The size shall be to suit |  |  |  |  |
| 20.1 | 610 x 610 x305 mm | Nos | 4 |  |  |
| 20.2 | 450 x 450 x305 mm | Nos | 1 |  |  |
| 21 | Supply installation testing and balancing of continous Perforated Stainless Steel Grilles for supply and return air grilles in accordance with the approved shop drawings size 610 x 610 mm & 450 x 450 mm | SQM | 2 |  |  |
| 22 | Supply, installation, testing and comissioning of Inline Centrifugal duct fan with dynamically balanced impeller of 500cfm capacity, min 10 mm static , complete with GI box, with single phase direct driven motor with class B, IP44 protection with an internal automatic safety thermal overload protection, dynamically balanced impeller of following capacity, with an operating sound level of less than 55dB at 3 m distance. | Nos | 1 |  |  |
|  | TOTAL PART VI A |  |  |  |  |

| TOTAL PART VI B Air Conditioning Works - Surgical Complex, Mananthavady |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item No. | Description of items | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
|  | MACHINERY |  |  |  |  |
| 1 | Supply, intallation, testing and commissioning (SITC) of 5.5 TR capacity aircooled Outdoor condensing unit with scroll compressor as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, hermetically sealed scroll compressor, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, high-low pressure cut out, suitable for three phase 440V supply. | No | 2 |  |  |
| 2 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 5.5TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition |  |  |  |  |
| a | Suction Line | RM | 30 |  |  |
| b | Liquid Line | RM | 30 |  |  |
| 3 | SITC of DX type double skinned air handling units,ceiling suspended/floor mounting type 5.5 TR, 1000 lps capcity complete with suitable DIDW blower (asper approved make), blower section, static pressure of 80mm of water column, built in pre filter(EU4), fine filter(EU7) and controls connected to condensing units, insulated SS drain pan, 6 row cooling coil, electric motor, belt drive package with TEFC motor class 'B' insulation, suitable for 3 phase, 415 V, 50Hz supply, suitable AHU panel, ARI certified, belt guards, with 0.6mm double skinned 40mm thick PUF panel, suitable supports for suspending from slab, vibration isolator, etc. conforming to specifications. The air handling units shall have 1 inlet refrigerant coils and 1 outlet refrigerant coils suitable for 1 numbers of 5.5 TR capacity ODU and shall conform to specifications. | No | 2 |  |  |
| 4 | Supply, installation, testing and commissioning of Air Cooled High Wall mounted Split Air Conditioner of following capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, standard 5 m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 5m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit, ODU MS stand, first charge refrigarant gas, suitable stabilizer etc complete as required. |  |  |  |  |
| 4.1 | 1.5 TR 5 star rated as per BEE | Each | 5 |  |  |
| 4.2 | 2 TR 4 star rated as per BEE | Each | 4 |  |  |
| 5 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping with 13 mm nitrile rubber insulation and electrical connection interconnecting the condensing unit to evaporating unit for split AC's as per site condition | RM | 22 |  |  |
| 6 | Supply, Laying and Fixing of control wiring of suitable size required from the Indoor to outdoor units for all units as per specification. | RM | 18 |  |  |
| 7 | Supply, installation, testing and commissioning PVC drain pipe of 25mm dia ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification | RM | 17 |  |  |
| 8 | SITC of Humidity Controller electric strip heaters in supply air plenum complete with fixing arrangements, thermostats and safety thermostat including all power and control wiring | No | 1 |  |  |
|  | AIR DISTRIBUTION |  |  |  |  |
| 9 | Supply, installation, testing and commissioning of factory fabricated rectangular Aluminum sheet metal ducting for Supply/return/fresh air duct/collar connecting to indoor unit as per ducting specifications and with suitable supports using MS angles, channels, rods, anchor bolts, etc to roof /truss as per IS 655 and as per specifications. |  |  |  |  |
| 9.1 | 20 G | SQM | 49 |  |  |
| 9.2 | 22 G | SQM | 201 |  |  |
| 10 | Supply, installation, testing and commissioning of factory fabricated rectangular GSS sheet metal ducting for Supply/return/fresh air duct/collar connecting to indoor unit as per ducting specifications and with suitable supports using MS angles, channels, rods, anchor bolts, etc to roof /truss as per IS 655 and as per specifications. |  |  |  |  |
| 10.1 | 22 G | SQM | 7 |  |  |
| 10.2 | 24 G | SQM | 20 |  |  |
| 11 | SITC of External thermal insulation on supply air ducts using min 13mm thick nitrile rubber class "O" closed cell type with antimicrobial protection as per specifications | SQM | 227 |  |  |
| 12 | Supply, installation, testing and commissioning of Acoustic duct lining using 10mm nitrile rubber insulation open cell type inside the ducts, antimicrobial protection at the outlets of all indoor units upto 4m distance from fan outlet as per spec provided. | SQM | 49 |  |  |
| 13 | Supply, installation and comissioning of underdeck insulation with 20 mm thick closed cell elastomeric Nitrile Rubber density of 40kg/m3 on ceiling with necessary adhesive, 600X600mm GI netting, fixtures, supports etc. | SQM | 9 |  |  |
| 14 | Supply, fabrication, installation, testing of flexible connections made out of fire resistant flexible double canvas sleeve. | Set | 2 |  |  |
| 15 | Supply, installation, testing and comissioning of Powder coated extruded aluminimum Continuous grilles 16mm frame, as per spec | SQM | 5 |  |  |
| 16 | SITC of Fire Control Damper made of 16G GSS sheet blade and frame with 165mm casing, heavy duty interlocking blades and fuly enclosed bade linkage mechanism, SS lateral seal blade seals, self lubricating sintered bronze bushes, fire rating as per UL555-1995 tested as per BS-476 part 20 with 18G extended sleeve 450mm and with fusible link, spring mechanism control panel temp sensor, smoke sensor, limit swith with lever for auto shut off in case of fire/smoke as per specifications. | SQM | 1 |  |  |
| 17 | SITC of multi blade type volume control dampers made of extruded auminium for ducts/ collars to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distributions system in main ducts, return ducts & other area as per specification. | SQM | 4 |  |  |
| 18 | SITC of Fresh air GI louvers of size 300x300 mm with wire mesh and birds screen for IDUs/AHUs as per specifications. | SQM | 2 |  |  |
| 19 | Supply and fixing of Terminal HEPA Filters having filtering efficiency of 99.7% down to 0.3 microns with aluminum frame works, suitable for fixing in the Supply air plenum boxes |  |  |  |  |
| 19.1 | 610 x 610 x305 | Nos | 8 |  |  |
| 19.2 | 450 x 450 x305 | Nos | 1 |  |  |
| 20 | SITC of Plenum box made of 18G Aluminum sheet with frame work for fixing HEPA filters at terminalsand provision of access door for removing the HEPA Filters for cleaning and replcaement .The size shall be to suit |  |  |  |  |
| 20.1 | 610 x 610 x305 mm | Nos | 8 |  |  |
| 20.2 | 450 x 450 x305 mm | Nos | 1 |  |  |
| 21 | Supply installation testing and balancing of continous Perforated Stainless Steel Grilles for supply and return air grilles in accordance with the approved shop drawings size 610 x 610 mm & 450 x 450 mm | SQM | 4 |  |  |
| 22 | Supply, installation, testing and comissioning of Inline Centrifugal duct fan with dynamically balanced impeller of 500cfm capacity, min 10 mm static , complete with GI box, with single phase direct driven motor with class B, IP44 protection with an internal automatic safety thermal overload protection, dynamically balanced impeller of following capacity, with an operating sound level of less than 55dB at 3 m distance. | Nos | 1 |  |  |
|  | TOTAL PART VI B |  |  |  |  |

| TOTAL PART VII Medical Gas Surgical Block & Gynec Block |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl. No. | Description of item | Unit | Qty | Rate(in Words and Figures) | Amount (in Words and Figures) |
| 1 | Solid drawn, seamless, deoxidised, non- arsenical, half hard, tempered and degreased copper pipes-As per specification |  |  |  |  |
|  | 54 mm OD x 1.2mm thick | MTRS | 60 |  |  |
|  | 42 mm OD x 1.2 mm thick | MTRS | 200 |  |  |
|  | 28 mm OD x 0.9 mm thick | MTRS | 120 |  |  |
|  | 22 mm OD x 0.9 mm thick | MTRS | 350.00 |  |  |
|  | 15 mm OD x 0.9 mm thick | MTRS | 500.00 |  |  |
|  | 12 mm OD x 0.7 mm thick | MTRS | 200.00 |  |  |
| 2 | Gas Outlet Points/ Terminal Unit : Supply,Installation, testing and commissioning of Gas outlet points for Oxygen, Air,Vacuum and Nitrous Oxide . As per specifiation |  |  |  |  |
|  | Oxygen outlet with probe | NOS | 52 |  |  |
|  | Air outlet with probe | NOS | 30 |  |  |
|  | Vacuum outlet with probe | NOS | 52 |  |  |
|  | Nitrous Oxide outlet with probe | NOS | 18 |  |  |
| 3 | Bed Head Horizontal Wall Panel -As per technical Specification | NOS | 16 |  |  |
| 4 | Rigid Pendant : Supply,Installation, testing and commissioning of rigid pendant | NOS | 6 |  |  |
| 5 | Isolation Valves |  |  |  |  |
|  | 15 mm ball valve | NOS | 27 |  |  |
|  | 22 mm ball valve | NOS | 14 |  |  |
| 6 | MEDICAL GAS ALARM PANEL : Supply, Installation, testing and commissioning of Medical Gas Alarm Panel- |  |  |  |  |
|  | Alarm panel 2services (Oxygen, and Vacuum) | NOS | 2 |  |  |
|  | Alarm panel 3 services (Oxygen, Air, and Vacuum) | NOS | 2 |  |  |
|  | Alarm panel 4 services (Oxygen, Air, Vacuum and Nitrous Oxide) | NOS | 1 |  |  |
| 7 | Oxygen Control Panel : Supply, Installation testing and commissioning of Fully Automatic Oxygen Control panel.As per tender technical specifications | SET | 1 |  |  |
| 8 | Oxygen Manifold (2x15) Supply, Installation, Testing and Commissioning of Oxygen Manifold. .As per technical specification | SET | 1 |  |  |
| 9 | Emergency Oxygen Supply System : Supply, Installation, testing and commissioning of (2x2 size) cylinder Emergency Oxygen Supply System as per technical specifications. | SET | 1 |  |  |
| 10 | Nitrous Oxide Control System : Supply, Installation testing and commissioning of Semi Automatic Nitrous Oxide Control Panel System.As per tender technical specifications | SET | 1 |  |  |
| 11 | Nitrous Oxide Manifold (2x6) Supply, Installation, Testing and Commissioning of Nitrous Oxide Manifold. .As per technical specification | SET | 1 |  |  |
| 12 | Oxygen Flow meter with Humidifier Bottle and Oxygen probe - Supply installation, testing and commissioning of oxygen flow meter with humidifier bottle 0-10Litres. As per tender technical specifications | NOS | 50 |  |  |
| 13 | Medical Vacuum Plant Package Duplex vacuum pumps: Supply installation testing and commissining of Medical vacuum plant as per tender specification | SET | 1 |  |  |
| 14 | Ward Vacuum Unit : Suply installation testing and commissiong of Ward suction unit with suction probe. As per Technical specifications. | NOS | 50 |  |  |
| 15 | Portable Theatre Vacuum Unit : Suply installation testing and commissiong of portable theatre suction unit with suction probe. As per Technical specifications. | NOS | 6 |  |  |
| 16 | Air Compressor: Suply installation testing and commissiong of duplex air compressor system (including electric control panel)As per Technical specifications | NOS | 1 |  |  |
| 17 | Supply of O2 cylinders -Extra | NOS | 25 |  |  |
| 18 | Supply of Nitrous Oxide cylinders -Extra | NOS | 12 |  |  |
| 19 | Electric wiring inside the gas manifold and plant room (Hospital will provide three phase power cable at one point) | LOT | 1.00 |  |  |
|  | TOTAL PART VII |  |  |  |  |