## Electrical - Abstract
CONSTRUCTION OF NEW OP BLOCK AT GOVERNMENT GENERAL HOSPITAL, KOZHIKKODE
PART B -ELECTRICAL WORKS
S.No | DSR No | Item Description | Unit | Qty | Rate Rs in figures&words | Amount in Rs
1 | 1.10 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5Sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required | Point | 125
2 | 1.11 | Wiring for twin control light point with 1.5Sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required | Point | 2
3 | 1.14 | Circuit Sub main wiring in PVC Conduit : Wiring for circuit sub main wiring alongwith earthwire with the following sizes of PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
a | 1.14.1 | 2x1.5 sq mm +1x1.5 sq. mm earth wire | Rm | 450
b | 1.14.2 | 2x2.5 sq mm +1x 2.5 sq.mm earth wire | Rm | 650
c | 1.14.3 | 2x4 sq mm +1x4 sq.mm earth wire | Rm | 500
d | 1.14.8 | 4x4 sq mm + 2x4 sq mm earth wire | Rm | 50
e | 1.14.10 | 4x10 sq mm + 2x10 sq mm earh wire | Rm | 50
4 | 1.18 | Supplying and drawing 2 pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. | Rm | 180
5 | 1.19 | T.V. Cable in existing conduit : Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | Rm | 50
6 | 1.21 | S/F PVC conduit : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 1.21.1 | 20 mm | Rm | 160
b | 1.21.2 | 25 mm | Rm | 140
7 | 1.22 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
a | 1.22.7 | 200mm x 150mm x 60mm deep | Each | 5
8 | 1.24 | S/F Modular type switch/ socket : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc as required.
a | 1.24.6 | Telephone socket outlet | Each | 15
b | 1.24.7 | TV antena socket outlet | Each | 2
9 | 1.25 | Supplying and fixing electronic fan regulator : Supplying and fixing stepped type electronic fan regulator on the existing odular plate and switch box excluding modular plate but including connections etc as required. | Each | 42
10 | 1.26 | S/F Modular type blanking plates : Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 10
11 | 1.27 | S/F Modular boxes, base & cover plate : Supplying and fixing following size/ modules,GI box along with modular base, cover plate for modular switches in recess etc as required.
a | 1.27.1 | 1 or 2 module( 75 mmx75 mm) | Each | 15
12 | 1.31 | S/F light plug point modular type accessories : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection,painting etc as required, (For light plugs to be used in non residential buildings ) | Each | 72
13 | 1.32 | S/F Power plug point with modular type switch : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each | 24
14 | 1.33 | S/F Ceiling rose : Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each | 90
15 | 1.38 | S/F call bell/ buzzer : Supplying and fixing call bell / buzer suitable for D.C / A.C single phase, 230 volts, complete as required. | Each | 10
16 | 1.41 | ITC Fluroscent fitting directly on surface : Installation testing and commissioning of pre- wired, fluroscent fitting/ compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq mm FR PVC insulated, copper conductor, single core cable and earthing etc as required. | Each | 62
17 | 1.44 | ITC Ceiling fan : Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length { Up to 30 Cm } with 1.5 sq mm FR PVC insulated, copper conductor, single core cable as required. | Each | 42
18 | 1.47 | Extra down rod 15 mm dia : Supplying and fixing extra down rod of 10 Cm length G. I pipe, 15 mm dia, heavy guage including painting etc. as required ( Note: More than 5 Cm length shall be rounded to the nearest 10 Cm and 5 Cm or less shall be ignored) | Each | 36
19 | 1.5 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
a | 1.50.1 | Upto 450 mm sweep | Each | 7
20 | 2.4 | S/F TPMCB DB : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a | 2.4.5 | 6 way, Double door | Each | 2
b | 2.4.6 | 8 way, Double door | Each | 2
21 | 2.1 | S/F 'C' series, MCB : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.10.1 | Single pole | Each | 47
b | 2.10.4 | Triple Pole | Each | 3
22 | 2.11 | S/F SP MCB blanking plate : Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 13
23 | 2.13 | S/F FP MCB isolator : Supplying and fixing following rating, four pole,415 Volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.13.1 | 40 amps | Each | 2
b | 2.13.2 | 63 amps | Each | 1
24 | 2.15 | S/F FP RCCB : Supplying and fixing following rating, four pole, 415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.15.1 | 25 amps | Each | 2
b | 2.15.2 | 40 amps | Each | 2
c | 2.15.3 | 63 amps | Each | 1
25 | 2.18 | S/F 20A SPN MCB industrial socket outlet : Supplying and fixing 20 amps, 240 Volts, SPN industril type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps 'C' series, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | Each | 6
26 | 5.4 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 2
27 | 5.9 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | Rm | 15
28 | 5.15 | Providing and fixing 25 mm X 5 mm G.I strip on surface or in recess for connections etc. as required | Rm | 60
29 | 7.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
a | 7.1.3 | Above 95 sq. mm and upto 185 sq. mm | Rm | 15
30 | 7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required
a | 7.7.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Rm | 120
b | 7.7.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Rm | 10
31 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a | 9.1.32 | 4 X 10 sq. mm | Each | 4
b | 9.1.34 | 4 X 25 sq. mm | Each | 4
c | 9.1.24 | 3.5 X 95 sq. mm | Each | 2
32 | LMR | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date
a |  | 4 x 10 sq. mm | Rm | 70
b |  | 4 x 25 sq. mm | Rm | 50
c |  | 3.5 x 95 sq. mm | Rm | 25
33 | LMR | Supplying and fixing following rating, 415 Volts, "C" series, miniature circuit breaker suitable for power loads of following poles in the existing MCB DB complete with connections, testing and commissioning etc as required.
a |  | 40A TP MCB | Each | 2
b |  | 63A TP MCB | Each | 1
34 | LMR | Supply of 1x28W fluorescent tube light fitting with powder coated CRCA sheet channel complete with all accessories, electronic ballast, lamp holder, 28W lamp etc as required. (Philips TMS540 HF / Wipro WRF 80128SG / GE LMS 28 N N) | Each | 58
35 | LMR | Supply of 1x28 W surface mounted mirror optic luminarie with all accessories like ballast, lamp, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (TCS 150 1xTL5-28W MI EBT / GE GETC 1x28 MOS HF / Equi) | Each | 2
36 | LMR | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod,suspension shackle,canopy etc with out regulator (Make:Usha Technix flair star rated / Equ). | Each | 42
37 | LMR | Supply of 250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/ shutters and all accessories as required complete. (Make:Usha Crisp Air / Equi.) | Each | 7
38 | LMR | Supply and fixing 400 mm sweep wall fan, swinging type with speed control and necessary adapter, of approved quality and colour. (Make:Usha - Maxx Air / Equi) | Each | 4
39 | LMR | S/F PVC Holder : Supplying and fixing PVC straight / angle batten holder including CFL lamp, connection etc. as required.
a |  | 15 watts | Each | 9
b |  | 20 watts | Each | 4
40 | LMR | Supply and Installation of 20 pair MDF box, back mount frame and original krone connectors with all accessories. | Each | 1
41 | LMR | Supplying and fixing 1x36W CFL Decorative compact street light luminaire with sheet steel aluminium housing, UV stabilized acrylic cover, aluminium reflector etc complete with all mounting accessories as required. The item shall also include suitable size lamp bracket fabricated out of B class G.I pipe to suit the lamp fitting with its clamping accessories as required. (Philips HGS120 1xTL5-28W EBE / Wipro WSF 14128 SG / Equ) | Each | 4
42 | LMR | Supply of 1x28W industrial Tube light fitting with reflector, CRCA sheet steel housing, ballast, lamp etc prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required. ( Philips TMS 122 M 1xTL5-28W EBE / Wipro WIF 91128 SG / GE GET CI 1x28 C/S HF) | Each | 2
43 | LMR | Supply, Installation, Testing & Commissioning of LT panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with busbars extendable on both sides, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
INCOMER
1 no. 160A, FP, AC23A, 415V, 50Hz switch disconnector fuse unit with Din type HRC fuse of suitable rating (as per fuse rating in meter board).
BUSBARS
1 Set of 200A TPN busbars of high conductivity electrolytic quality Aluminium alloy.
1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing.
INSTRUMENTS
1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 160/5A, Class 1.0, 10VA, Cast Resin CT
OUTGOING
2 nos 125A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.
6 nos. 63A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.
|  | 4 nos. 32A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.. | Each | 1
44 | LMR | Supply, Installation, Testing & Commissioning of Three phase meter box, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP54, wall / floor mounting, dust and vermin proof, powder coated, outdoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
SWITCHGEAR & OTHER ACCESSORIES
Space provision for accomodating 3 phase CT operated energy meter from KSEB with all connections, glass view panel, control MCB, lockable compartment etc.
3 nos. Suitable ratio CT (as per KSEB) with Acc. Class 0.5, 10VA in locakable compartment.
3 nos 160A rewireable type baklite fuse unit with 1 no. Neutral link.
1 no. 160A, FP, AC23A, 415V, 50Hz switch disconnector fuse unit with Din type HRC fuse of suitable rating (as per KSEB) in separate cubical.
|  | The meter board shall have 200 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy, earth bus of required size, 4P terminal connectors, control wiring with all reqiuired accessories complete. | Each | 1
45 | LMR | S/L 10 SWG copper wire in ground : Supplying and laying 10 SWG copper wire on surface / recess / groundloop earthing, including soldering connection / termination with Cu thimble etc as required | Rm | 200
46 | LMR | Supply and providing 6 mm thick & 1 m wide electrical grade chequered type rubber mat to withstand 3.3 KV dielectric strength conforming to IS 5429/ 1969. | Rm | 2
TOTAL PART B - ELECTRICAL WORKS
GRAND TOTAL - PART A + PART B