## abstract
CIVIL,ELECTRICAL,HVAC,FIRE PROTECTION SYSTEM AT MICROBIOLOGY LAB WITH BSL II FACILITY AT CHIEF DISEASE INVESTIGATION OFFICE, PALODE - PHASE - II WORKS
Part A
LANDSCAPING & ROAD WORKS
Item No | Description of Item | Quantity | Unit | Rate (in figures & words) | Amount
1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth, lead up to 50 m and lift up to 1.5 m, disposed earth to be levelled and neatly dressed. All kinds of soil. | 100 | Cu.m
2 | Providing and laying 60 mm thick factory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50 mm thick compacted bed of coarse sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge. | 196 | Sq.m
3 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature jointed with cement mortar 1:3 (1 cement : 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5 mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-Charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in- Charge). | 4.85 | Cu.m
4 | Painting kerb stone surface marking with adequate nos of coats to give uniform finish using external emulsion paint in zebra pattern, including cleaning the surface of all dirt, scales, oil, grease and foreign material etc. complete. | 19.5 | Sq.m
5 | Grassing with Zoysia grass (Mexican Grass) including watering and maintenance of the lawn for 30 days or more till the grass forms a thick lawn free from weeds and fit for mowing including supplying good earth if needed (the good earth shall be paid for separately) including preparation of bed, etc. | 330 | Sq.m
6 | Supplying and stacking at site dump manure from approved source, including carriage upto 1 km (manure measured in stacks will be reduced by 8% for payment) : | 6 | Cu.m
7 | Supply and planting flowering and foliage plants like Ixora, Hibiscus, Tabarnia mundane, Hemilia patten, crotons, etc. | 150 | Each
8 | Formation of shrubbery with flowering and foliage shrubs like Arelia, Execaria, Acaalifa, Hibiscus, Etc. | 50 | Sq.m
9 | Supply and Planting Fox tail Palm 6' | 10 | Each
10 | Supply and Planting Red Palm 2' | 2 | Each
11 | Supplying,stacking and Spreading good Earth for Landscaping work | 18 | Cu.m
12 | Grassing with Buffalo grass including watering and maintenance of the lawn for 30 days or more till the grass forms a thick lawn free from weeds and fit for mowing including supplying good earth if needed (the good earth shall be paid for separately) including preparation of bed, etc. | 271 | Sq.m
13 | Supplying and Planting Following in door plants
a | Rapish Palm 4' | 3 | Each
b | Rapish Palm 6' | 3 | Each
c | Aglomia 1' | 10 | Each
d | Seculance | 10 | Each
e | Agaiva | 8 | Each
RETAINING WALL & GATE
14 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | 28.5 | Cu.m
15 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | 8 | Cu.m
16 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size). | 4 | Cu.m
17 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) upto plinth level with : Cement mortar 1:6 (1 cement : 6 coarse sand) | 20.3 | Cu.m
18 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level. 1:1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size). | 2.11 | Cu.m
19 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. up to floor five level excluding cost of centering, shuttering, finishing and reinforcement. 1:1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size). | 1.1 | Cu.m
20 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete Thermo Mechanically Treated bars | 481.5 | Kg
21 | Centering and shuttering including strutting, propping etc. and removal of form for :
a | Foundations, footings, bases of columns, etc. for mass concrete | 6.6 | Sq.m
b | Columns, Pillars, Piers, Abutments, Posts and Struts | 13.7 | Sq.m
22 | Brick work with F.P.S bricks of class designation 75 in superstructure above plinth level upto floor V level in cement mortar 1:6 (1 cement: 6 coarse sand) | 3.5 | Cu.m
23 | 12 mm cement plaster of mix 1:6 (1 cement : 6 fine sand). | 15 | Sq.m
24 | 15mm cement plaster on rough side of single or half brick wall of mix 1:6 (1 cement : 6 fine sand) | 26 | Sq.m
25 | Pointing on stone work with cement mortar 1:3 (1 cement: 3 fine sand) :Flush/ Ruled/Struck or weathered pointing | 13.5 | Sq.m
26 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade. Two or more coats on new work | 54.5 | Sq.m
27 | Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface. | 54.5 | Sq.m
28 | Providing and fixing MS Gate of approved design including locking arrangements, two coats of Zinc chromate primer etc. etc complete as per the direction of Engineer in charge | 200 | Kg
29 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade: Two or more coats on new work over an under coat of suitable shade with ordinary paint of approved brand and manufacture | 10.8 | Sq.m
30 | Demolishing brick work manually / by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-Charge. In cement mortar | 1.7 | Cu.m
31 | Demolishing stone rubble masonry manually / by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in- Charge. In cement mortar | 9.6 | Cu.m
VIEW PANELS
32 | View panel both side flushed with glasses hermetically sealed (moisture removed) as per manufacturer's standard and as per sample approved. Size (W x H) in mm
(To suit on masonary wall) double glass view panel flushed both sides .
a | 1500mm width and 1200mm depth | 4 | Each
b | 1200mm width and 1200mm depth | 1 | Each
c | 900mm width and 1200mm depth | 3 | Each
HVAC
MACHINERY
33 | Supply, intallation, testing and commissioning (SITC) of 8.5 TR capacity aircooled Outdoor condensing unit with scroll compressor as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, hermetically sealed scroll compressor, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, high-low pressure cut out, power and control cabling from nearest isolator and between out door and indoor units suitable for three phase 440V supply. | No | 1
34 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 8.5TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition | RM | 16
35 | SITC of DX type double skinned air handling units, floor mounting type 8.5 TR, 1700 lps capcity complete with suitable DIDW blower (asper approved make), blower section, static pressure of 125mm of water column, built in pre filter(EU4) and fine filter(EU7) and controls connected to condensing units, insulated SS drain pan, 6 row cooling coil, electric motor, belt/direct drive package with TEFC motor class 'B' insulation, suitable for 3 phase, 415 V, 50Hz supply, suitable AHU panel with cabling, ARI certified, belt guards, digital temperature humdity sensor and pressure gauges at clean rooms, suitable supports, vibration isolators, etc. conforming to specifications. The air handling units shall have 1 inlet refrigerant coils and 1 outlet refrigerant coils suitable for 1 numbers of 8.5 TR capacity ODU and shall conform to specifications. | No | 1
36 | Supply, intallation, testing and commissioning (SITC) of 3 TR capacity aircooled Outdoor condensing unit with scroll compressor as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, hermetically sealed scroll compressor, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, high-low pressure cut out, power and control cabling from nearest isolator and between out door and indoor units suitable for three phase 440V supply. | No | 1
37 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 3TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition | RM | 30
38 | SITC of DX type double skinned air handling units, ceiling suspended type 3 TR, 600 lps capcity complete with suitable DIDW blower (asper approved make), blower section, static pressure of 50mm of water column, built in pre filter(EU4) & fine filter(EU7) and controls connected to condensing units, insulated SS drain pan, 6 row cooling coil, electric motor, belt/direct drive package with TEFC motor class 'B' insulation, suitable for 3 phase, 415 V, 50Hz supply, suitable AHU panel with cabling, ARI certified, belt guards, digital temperature humdity sensor and pressure gauges at sterile areas, suitable AHU supports, vibration isolators, etc.. conforming to specifications. The air handling units shall have 1 inlet refrigerant coils and 1 outlet refrigerant coils suitable for 1 numbers of 3TR capacity ODU and shall conform to specifications. | No | 1
39 | Supply, Installation, Testing & Commissioning of sheet metal sectionalised construction double skin 0.8mm thick pre coated GI Treated fresh air & exhaust air treatment units (TFEA) complete with 40mm thick injected PUF insulation of density not less than 38Kg/CuM. Unit shall comprise of supply air stream (lower tier) comprising of pre-filter section with 50mm thick synthetic fibre filters, fine filter section with 300mm thick fine filters, exhaust air stream (upper tier) comprising of fine filter section with 200mm thick and hepa filter 300mmtick, heat recovery section complete with HEAT PIPE (copper tube Finned coil) one for fresh air and another for exhaust with fluid from from exhaust coil (recovers the heat) to fresh air coil (air is cooled) for heat recovery. Fluid within heat pipe shall be refrigerant filled and sealed between sections. Fan section & associated motor and complete with DIDW backward curved centrifugal fan of static 40mm for fresh air and 80mm for exhaust, suitable 3 phase 415V 50Z suppy, TEFC sq.cage motor belt drive package, AHU panel with cabling from panel to unit, suitable vibration isolatior. The fan outlet velocity shall not exceed 2000fpm. The TFA units shall be selected as per the design duty conditions and provided with thermal break profile The air path is independant circuit for fresh air and exhaust air to avoid cross contamination.
39.1 | 500 lps fresh air & exhaust air | No | 1
40 | Supply, installation, testing and commissioning of Air Cooled High Wall mounted Split Air Conditioner of following capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, standard 4 m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 4m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit, ODU MS stand, first charge refrigarant gas, suitable stabilizer etc complete as required.
40.1 | 2 TR 4 star rated as per BEE | Each | 1
40.2 | 1.5 TR 5 star rated as per BEE | Each | 3
41 | Supply, Laying and Fixing of 4C 4Sq.mm size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor cable conforming to IS 7098 (Part 1) amended upto date with brass compression glands on surface/ cable tray/ wall / build in trench etc as required from the Indoor to outdoor units of all units for control wiring. | RM | 18
42 | Supply, installation, testing and commissioning PVC drain pipe of 25mm dia ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification | RM | 25
43 | Supply and fixing Heater package with Humidistat and contactor for humidity control | No | 1
AIR DISTRIBUTION
44 | Supply, installation, testing and commissioning of factory fabricated rectangular Clean Room Ducting made out of 120GSM GSS duct with TDF joints and with gasketing and leak tested with TiCl4 / air pressure. Ducting provided with Silicon sealent at all flange joints. Including supports using MS angles, channels, rods, anchor bolts and with suitable supports to concrete ceiling / roof/ walls as supply return and riser ducts.
44.1 | 20 G | SQM | 5
44.2 | 22 G | SQM | 18
44.3 | 24 G | SQM | 313
45 | SITC of External thermal insulation on supply air ducts using min 12mm thick nitrile rubber class "O" closed cell type with antimicrobial protection and aluminium foil vapour barrier as per specifications | SQM | 313
46 | Supply, installation, testing and commissioning of Acoustic duct lining using 10mm nitrile rubber insulation open cell type inside the ducts, antimicrobial protection at the outlets of all indoor units upto 4m distance from fan outlet as per spec provided. | SQM | 22
47 | Supply, fabrication, installation, testing of flexible connections made out of fire resistant flexible double canvas sleeve. | Set | 2
48 | Supply, installation, testing and comissioning of Powder coated extruded aluminimum Continuous grilles 16mm frame, 15deg deflection for supply / return air 150mm wide as per spec | SQM | 6
49 | SITC of Powder coated extruded aluminimum perforated square diffusers both side coated with collar damper aluminuim extruded black anodized . (300mmX300mm/450mmx450mm /600mmx600mm) | SQM | 2
50 | SITC of Powder coated extruded aluminium return air perforated square diffusers both side coated without VCD. (300mmX300mm/450mmx450mm/600mmx600mm) | SQM | 2
51 | SITC of Fire Control Damper made of 16G GSS sheet blade and frame with 165mm casing, heavy duty interlocking blades and fuly enclosed bade linkage mechanism, SS lateral seal blade seals, self lubricating sintered bronze bushes, fire rating as per UL555-1995 tested as per BS-476 part 20 with 18G extended sleeve 450mm and with fusible link, spring mechanism control panel temp sensor, smoke sensor, limit swith with lever for auto shut off in case of fire/smoke as per specifications. | SQM | 1
52 | SITC of multi blade type volume control dampers made of extruded auminium for ducts/ collars to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distributions system in main ducts, return ducts & other area as per specification. | SQM | 2
53 | SITC of Fresh air GI louvers of size 300x300 mm with wire mesh and birds screen for IDUs/AHUs as per specifications. | SQM | 3
54 | Supply and fixing of Terminal HEPA Filters having filtering efficiency of 99.7% down to 0.3 microns with aluminum frame works, suitable for fixing in the Supply air plenum boxes
54.1 | 600 x 600 x305 | Nos | 2
54.2 | 450 x 450 x305 | Nos | 10
55 | SITC of Plenum box made of 18G Aluminium sheet with frame work for fixing HEPA filters at terminals and provision of access door for removing the HEPA Filters for cleaning and replcaement .The size shall be to suit
55.1 | 600 x 600 x305 mm | Nos | 2
55.2 | 450 x 450 x305 mm | Nos | 10
56 | Supply installation testing and balancing of continous Perforated Stainless Steel Grilles for supply and return air grilles in accordance with the approved shop drawings size 600 x 600 mm & 450 x 450 mm | SQM | 6
57 | SITC of Air curtain of capacity min 900lps, 8mps velocity 1500mm wide suitable for 230V/50Hz, sound level not exceeding 55dB at 1m | Nos | 2
Note:- | Scope of work includes testing of the clean room including air balancing, particle count and DOP test for Hepa Filter to achieve BSL II class clean room requirements.
FIRE PROTECTION SYSTEM
DOWN COMER/SPRINKLER SYSTEM
58 | Supplying, Installation, testing and commissioning of electric driven pump (terrace pump) sets suitable for automatic operation incase of pressure drop and consisting electrical control panel with DOL Starter, panel and accessories of the following complete in all respect as required, Pump rated for 900lpm, 35m head Monobloc type, C.I body volute type coupled with suitable HP SQ cage induction motor,sychoronous speed 2900rpm, suitable for operation on 415V, 3phase 50Hz, AC with IP 55 class of protection for enclosure, horizontal foot mounted type with class F insulation, M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required.Suitable cement concrete foundation duly plastered with anti vibration pads. | Nos | 1
59 | Supply, installation, testing and commissioning of pressure gauge 0-200 PSI ( 0 - 14 Kg ) range, 3/8" BSP bottom entry, 4" dial weather proof with stainless steel internals, siphon tube amd ball valve including fittings, etc. complete as required. | Nos | 1
60 | Supply, installation, testing and commissioning of industrial type pressure switch having 1/4" BSP(F) connection IP:32 enclosure protection, phosphor bronze bellows as sensing element, SDPT contact system, switch rating 6A Inductive/lOA resistive 380 V AC, 0.2A Inductive/10A resistive 250V DC suit with ball valve etc. complete as required. | Nos | 1
61 | Supply, and fixing of Air release valve all riser pipes as per specification | Nos | 1
62 | Providing, laying, welding, testing & commissioning of 'C' class medium duty MS pipe conforming to IS 3589 and 1239 including drop forged fittings like elbows, tees flanges, tapers, nuts bolts, gaskets etc.., fixing the pipe on the wall/ceiling with suitable clamps and painting with primer and two or more coats of synthetic enamel paint of required shade complete as required.
62.1 | 100 mm dia | metre | 25
62.2 | 40 mm dia | metre | 20
62.3 | 25 mm dia | metre | 40
63 | Supplying and fixing, testing & commissioning of butterfly valve of rating PN 1.0 with cast Iron body, SG Iron seat ISI marked complete with nuts, bolts, washers, gaskets, conforming to IS 13095 following sizes as required.
63.1 | 100 mm dia | no | 1
63.2 | 40 mm dia | no | 2
64 | Supplying, fixing, testing & commissioning of dual plate non-return valve of following sizes confirming to IS : 5312 complete with rubber gasket, GI bolts, nuts, washers etc. as required.
64.1 | 100 mm dia | Nos | 1
65 | Supplying, fixing, testing & commissioning of foot valve complete with bolts, nuts, washers and rubber gaskets etc. conforming to IS:4038 (ISI marked) of sizes:
65.1 | 100 mm dia | Nos | 1
66 | Supply, installation, testing, and commissioning of sprinkler bulbs having a temperature rating of 68 degree centigrade | Nos | 25
67 | Supply, installation, testing and commissioning of gun metal fire hydrant valve, single headed oblique type 63 mm instantaneous outlets with female socket for hose connection and inlet side with flange suitable for 100 mm pipe flange, valve conforming to 1S:5290 complete with blank cap chain, etc | Nos | 1
68 | Supplying and fixing First-aid Hose Reel with MS construction spray painted in Post office Red, conforming to IS 884 with up to date amendments, complete with the following as required. (a) 30 m. long 20 mm (nominal internal dia water hose Thermoplastic (Textile reinforced) Type-2 as per IS: 12585 (b) 20 mm (nominal internal ) dia gun metal globe valve & nozzle. (c) Drum and brackets for fixing the equipments on wall. (d) Connections from riser with 40 mm dia stop valve (gun metal) & M.S. Pipe | set | 1
69 | Supplying and fixing 63 mm dia, 15 mtr. Long RRL hose pipe with 63 mm dia Male and Female Gun metal couplings duly binded with GI wire, rivets etc. conforming to IS 636 (type-A) as required. | Nos | 2
70 | Supplying & fixing 63 mm dia Gun metal branch pipe with 20 mm (nominal internal diameter) size Gun Metal nozzle conforming to IS 903, suitable for instantaneous connection to inter-connect hose pipe coupling as required. | Nos | 1
71 | Supply, installation, testing and commissioning of hose boxes wall/pedestal type of size 750 x 250 x 600 mm made out of 16 SWG MS sheet steel with front side glass, locking arrangement and painted with approved colour completed as required and as per specifications. | Nos | 1
72 | Supply, installation, testing and commissioning of Fire brigade collective breaching with 4 nos. of (twin Siamese) flanged out let connection and built in check valves complete as required. | set | 1
FIRE ALARM SYSTEM
73 | Supply, installation, testing and commissioning of Addressable type Manual Call Point (break glass type) complete with push button, enclosed in box with provision for cable or conduit coupling. The unit to be painted fire red outside, white inside and written 'In case of fire break glass'. | Nos | 1
74 | Supply, installation, testing and commissioning of Hooter cum Speaker at different locations complete with all fixing accessories, etc. under false ceiling, roof, wall, 100dB sound level etc, with a time delay of max 30sec, interconnecting lo loop cable complete as required. | Nos | 1
75 | Supply, Installation, Testing & Commissioning of 16 bit intelligent Addressable Fire Alarm Panel with 1 loops ( each loop accessing at least 120 detectors ) including battery backup. The panel shall be microprocessor based with its own micro controller, memory, communication module and fire device loop
interface cards for intelligent initiating and indicating devices and should also be networkable in peer-to-peer basis with other Addressable Fire Alarm Panels. The Panel shall be able to give pin point location of all Fire/Fault conditions of addressable units via the address codes for each unit. The Panel shall also be able to automatically switch off all Control Switches when ever any Alarm is triggered.
The panel shall have 54 Ah SMF Battery, Keypad operation, L C D unit to indicate Fire / Fault Signal of individual unit, in built printer to log all incoming data etc complete in all respects. operation of speakers. Panel shall have :
The Panel shall also have Logic hardware and software built into it for initiating specific AHU tripping, time delay operation of hooter and others as follows :
(a) programming software for the system
(b) automatic system test activates
(c) detector sensitivity adjustments
(d) alarm verification
(e) Alpha/numerical display
(f) provision to connect to PCs and external printers
| (g) Support modbus and bacnet protocol. | Nos | 1
76 | Supply, installation, testing and commissioning of Analogue Addressable type Optical Smoke Detector (photoelectric type) complete with all accessories like base. base box, etc. to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. | Nos | 25
77 | Supply, installation, testing and commissioning of Analogue Addressable type Heat Detector (photoelectric type, Fixed cum-rate of rise type) with range unto 60 deg C complete with all fixing accessories like base, base box, etc. to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. | Nos | 4
78 | Supply and laying of 2x 1.5sq.mm copper armoured FRLS cable ISI marked with proper clamping, supports and terminations. | Metre | 198
PORTABLE FIRE EXTINGUISHERS
79 | Supply & fixing of of Carbon-dioxide extinguisher on wall of ISI marked 4.5 Kg capacity made from brand new seamless steel cylinder, as per IS: 7285 and CCE approval, fitted with Discharge hose and horn and Wheel type valve with initial Charge as per IS: 15683-2006 specification, bearing ISI Mark | Nos | 5
TOTAL -PART A
PART B
Civil Works
Item No | Description of Item | Quantity | Unit | Rate (in figures & words) | Amount
1 | Dismantling wood work in frames, trusses, purlins and rafters up to 10 metres span and 5 metres height including stacking the material within 50 metres lead: Of sectional area 40 square centimetres and above. | 0.19 | Cu.m
2 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) at plinth level with : Cement mortar 1:6 (1 cement : 6 coarse sand) | 16.4 | Cu.m
3 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases up to floor five level excluding the cost of centering, shuttering, finishing and reinforcement, with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size). | 0.2 | Cu.m
4 | Centering and shuttering including strutting, propping etc. and removal of form for. Suspended floors, roofs, landings, balconies and access platform. | 1.8 | Sq.m
5 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete Thermo Mechanically Treated bars | 20 | Kg
6 | Brick work with F.P.S bricks of class designation 75 in superstructure above plinth level upto floor V level in cement mortar 1:6 (1 cement: 6 coarse sand) | 1.15 | Cu.m
7 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations, of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels.Granite of any colour and shade. Area of slab over 0.50 sqm. | 1.1 | Sq.m
8 | Extra for providing opening of required size & shape for wash basin/ kitchen sink in kitchen platform, vanity counter and similar location in marble/ granite/ stone work, including necessary holes for pillar taps etc. including moulding, rubbing and polishing of cut edges etc. complete. | 2 | Each
9 | Providing and fixing Pre-laminated medium density fibre board IS: 14587:1998 marked, with one side decorative lamination other side balancing lamination Grade-I (exterior grade) in shelves with screws and fittings wherever required, edges to be sealed with PVC edge bending tape 2.00 mm thick of approved brand (fittings to be paid separately). Pre-laminated with decorative lamination one side and other side balancing lamination exterior Grade - I MDF Board 18 mm thick confirming to IS:14587. | 17 | Sq.m
10 | Steel work welded in built up sections, trusses, frame work including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 8.3 | Kg
11 | Cement concrete 1:2:4 with 20mm broken stone for flooring concrete in labs | 3.85 | Cu.m
12 | Providing high performance seam less R-25CE of Endura or Equivalent epoxy resin floor system of hard wearing-durable, resistant to chemicls of approved colour 2mm thick including providing self levelling layer over hard concrete floorin one cc 1:2:4 with 20mm broken stone (cost of concrete will be paid seperately) | 86.8 | Sq.m
13 | Suspended walkable false ceiling with 75mm thick structural insulated sanwiched panels made with PUF insulation having density 40kg per cubic metre as core sandwiched between stainless steel sheet of thickness 0.6mm and grade SS 304-2B having 1200mm or suitable width with required length, consisting 'T'bar suspension type of frame work made with extruded aluminium perimeter channels and 3mm thick 1"x1"square tube extruded aluminium runners suspended with 6mm dia G.I rods from existing RCC slab. Rate shall include necessary cutouts for air supply and lluminaries complete with edge finishing. Silicon sealant shall be used at the joints. Ceiling system shall be suitable for loading upto 150kg/sq.m | 73.1 | Sq.m
14 | Providing and fixing false ceiling at all height including providing and fixing of frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) as per IS : 277and consisting of angle cleats of size 25 mm wide x 1.6 mm thick with flanges of 27 mm and 37 mm, at 1200 mm centre to centre, one flange fixed to the ceiling with dash fastener 12.5 mm dia x 50 mm long with 6 mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50 mm of required length with nuts & bolts of required size and other end of angle hanger fixed with intermediate G.I. channels 45x15x0.9 mm running at the spacing of 1200 mm centre to centre, to which the ceiling section 0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm each having lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in a direction perpendicular to G.I. intermediate channel with connecting clips made out of 2.64 mm dia x 230 mm long G.I. wire at every junction, including fixing perimeter channels 0.5 mm thick 27 mm high
| having flanges of 20 mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450 mm centre, with 25 mm long dry wall screws @ 230 mm interval, including fixing of gypsum board to ceiling section and perimeter channel with the help of dry wall screws of size 3.5 x 25 mm at 230 mm c/c, including jointing and finishing to a flush finish of tapered and square edges of the board with recommended jointing compound , jointing tapes , finishing with jointing compound in 3 layers covering upto 150 mm on both sides of joint and two coats of primer suitable for board, all as per manufacturer’s specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed, all complete as per drawings, specification and direction of the Engineer in Charge .12.5 mm thick tapered edge gypsum plain board conforming to IS: 2095- Part I. | 86 | Sq.m
15 | Providing and fixing tiled false ceiling of approved materials of size 595x595mm in true horizontal level, suspended on interlocking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills,light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size
| 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanized butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge. 12.5 mm thick square edge PVC Laminated Gypsum Tile of size 595x595 mm, made of Gypsum plasterboard, manufactured from natural gypsum as per IS 2095 part I and laminated with white 0.16 mm thick fire retardant PVC film on the face side and 12 micron metalized polyester on the back side with all edges sealed with the face side PVC film which goes around and wraps the edges and is bonded to the edges and the back side metalized polyester film so as to make the tile a completely sealed unit. | 69 | Sq.m
16 | 12 mm cement plaster of mix 1:4 (1 cement : 4 coarse sand). | 5.3 | Sq.m
17 | 15 mm cement plaster on the rough side of single or half brick wall of mix. 1:4 (1 cement : 4 coarse sand). | 3.8 | Sq.m
18 | Pointing on stone work with cement mortar 1:3 (1 cement: 3 fine sand) :Flush/ Ruled/Struck or weathered pointing | 21.85 | Sq.m
19 | Finishing with Epoxy paint (two or more coats) at all locations prepared and applied as per manufacturer's specifications including appropriate priming coat, preparation of surface, etc. complete to the inside walls of lab | 235 | Sq.m
20 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade : Two or more coats on new work | 112 | Sq.m
21 | Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface : Water thinnable cement primer | 25.6 | Sq.m
22 | Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete. | 3.8 | Sq.m
23 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require : White Vitreous China Surgeon type wash basin of size 660x460 mm with single 15 mm C.P. brass pillar taps with elbow operated lever Make:Hindware,Cera,Jaquar or equivalent | 2 | Each
24 | Providing and fixing PTMT towel ring trapezoidal shape 215 mm long, 200 mm wide with minimum distances of 37 mm from wall face with concealed fittings arrangement of approved quality and colour, weighing not less than 88 gms. | 2 | Each
25 | Providing and fixing PTMT liquid soap container 109 mm wide, 125 mm high and 112 mm distance from wall of standard shape with bracket of the same materials with snap fittings of approved quality and colour, weighing not less than 105 gms. | 2 | Each
26 | Supplying and fixing Glass blocks of approved design and size using the special adhesives as per the direction of engineer in charge | 6 | Sq.m
27 (a) | Double Leaf Stainless Steel Door Size-1800mm(W) x 2400mm (H) 45mm (THK) PUF Infill Door Leaf - 0.8mm Thk Stainless steel sheet Door Profile - 1.0 mm Thk Stainless steel sheet Double Glazed Vision Panel with 5mm clear glass (200 x 300mm) With one Door Closure and standard Hardware. Manfr. Metaflex | 3 | Each
(b) | Double Leaf Stainless Steel Door Size-1200mm(W) x 2400mm (H) 45mm (THK) PUF Infill Door Leaf - 0.8mm Thk Stainless steel sheet Door Profile - 1.0 mm Thk Stainless steel sheet Double Glazed Vision Panel with 5mm clear glass (200 x 300mm) With one Door Closure and standard Hardware. Manfr. Metaflex | 1 | Each
28 | Supply, Installation, testing and commissioning of Washing machine front load of 6Kg capacity with 800rpm and as per manufacturer's specifications including the cost of transporation, loading, unloading, installation charges etc. complete: Make:IFB, SAMSUNG, LG or Equivalent. | 1 | Each
29 | Supplying and fixing good quality wall paper of approved design including all materials complete(Basic rate of wall paper not less than 1000/m2) | 25.2 | Sq.m
30 | Providing and laying 60 mm thick factory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50 mm thick compacted bed of coarse sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge. | 458.5 | Sq.m
31 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature jointed with cement mortar 1:3 (1 cement : 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5 mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-Charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in- Charge). | 16.1 | Cu.m
32 | Painting kerb stone surface marking with adequate nos of coats to give uniform finish using external emulsion paint in zebra pattern, including cleaning the surface of all dirt, scales, oil, grease and foreign material etc. complete. | 64.5 | Sq.m
33 | Grassing with Zoysia grass (Mexican Grass) including watering and maintenance of the lawn for 30 days or more till the grass forms a thick lawn free from weeds and fit for mowing including supplying good earth if needed (the good earth shall be paid for separately) including preparation of bed, etc. | 86.5 | Sq.m
34 | Supplying and stacking at site dump manure from approved source, including carriage upto 1 km (manure measured in stacks will be reduced by 8% for payment) : | 0.87 | Cu.m
35 | Supplying,stacking and Spreading good Earth for Landscaping work | 2.6 | Cu.m
MISCELLANEOUS WORKS
36 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | 8.4 | Cu.m
37 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size). | 5.9 | Cu.m
38 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with: Cement mortar 1:6 (1 cement : 6 coarse sand). | 13.2 | Cu.m
39 | Brick work with F.P.S bricks of class designation 75 in superstructure above plinth level upto floor V level in cement mortar 1:6 (1 cement: 6 coarse sand) | 4.6 | Cu.m
40 | 12 mm cement plaster of mix for walls 1:4 (1 cement : 4 fine sand). | 27 | Sq.m
41 | 15 mm cement plaster on the rough side of single or half brick wall of mix.1:6 (1 cement : 6 fine sand). | 19.8 | Sq.m
42 | Finishing walls with Acrylic Smooth exterior paint of required shade.New work (Two or more coat applied @ 1.67 ltr/ 10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm). | 46.8 | Sq.m
43 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade: Two or more coats on new work. | 137 | Sq.m
44 | steel work welded in built up sections, trusses, frame work including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 757 | Kg
45 | Providing corrugated G.S. sheet roofing including vertical/ curved surface fixed with polymer coated J or L hooks, bolts and nuts 8 mm diameter with bitumen and G.I. limpet washers or with G.I. limpet washers filled with white lead, including a coat of approved steel primer and two coats of approved paint on overlapping of sheets complete (up to any pitch in horizontal/ vertical or curved surfaces), excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required.0.63 mm thick with zinc coating not less than 275 gm/ m2 | 57.9 | Sq.m
46 | Providing ridges or hips of width 60 cm overall width plain G.S. sheet fixed with polymer coated J or L hooks, bolts and nuts 8 mm dia G.I. limpet and bitumen washers complete. 0.63 mm thick with zinc coating not less than 275 gm/ m2. | 7.2 | Rm
47 | 40mm thick Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement, including cement slurry, but excluding the cost of nosing of steps etc. complete. | 30 | Sq.m
RAIN WATER FILTER CHAMBER AND UG SUMP
48 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | 5.7 | Cu.m
49 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | 1.85 | Cu.m
50 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size). | 1 | Cu.m
51 | Providing, hoisting and fixing up to floor five level precast reinforced cement concrete work in string courses, bands, copings, bed plates, anchor blocks, plain window sills and the like, including the cost of required centering, shuttering but excluding cost of reinforcement, with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size). | 1 | Cu.m
52 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete Thermo-Mechanically Treated bars. | 100 | Kg
53 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in:Cement mortar 1:6 (1 cement : 6 coarse sand) | 2.1 | Cu.m
54 | Brick work with F.P.S bricks of class designation 75 in superstructure above plinth level upto floor V level in cement mortar 1:6 (1 cement: 6 coarse sand) | 1.45 | Cu.m
55 | 12 mm cement plaster of mix for ouside walls 1:4 (1 cement : 4 coarse sand). | 17.2 | Sq.m
56 | cement plaster 1:3 (1 cement : 3 fine sand) finished with a floating coat of neat cement: 12 mm cement plaster. | 11.85 | Sq.m
57 | Finishing walls with Acrylic Smooth exterior paint of required shade.New work (Two or more coat applied @ 1.67 ltr/ 10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm). | 4.65 | Sq.m
58 | Providing and fixing unplasticised rigid P.V.C pipe conforming to IS Standards (pressure 4kg/cm2) in drainage lines including cutting and making good the walls,cutting and refilling of earth, jointing all etc complete: 110mm | 15 | Rm
59 | Providing and fixing PVC fittings and fixtures conforming IS specifications including cutting and making good the walls etc. complete
a | 110mm dia Plain Elbow | 3 | Each
b | 110mm dia Plain bend | 3 | Each
c | 110mm dia Offset | 2 | Each
60 | Providing and fixing PVC pipe conforming to IS Standards (pressure 6kg/cm2) complete including all fittings, fixtures, cutting,chasing in walls and making good the walls, testing of joints, concealing the pipes wherever required etc complete.
a | 32mm PVC Pipe | 12 | Rm
61 | Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete. 25 mm nominal bore. | 4 | Each
62 (a) | Supplying, filling, spreading & leveling stone boulders of size range 5 cm to 20 cm, in filter chamber of Rain wter tank, in the required thickness, for all leads & lifts, all complete as per direction of Engineer-in-charge. | 0.83 | Cu.m
(b) | Supplying, filling, spreading & leveling gravels of size range 5 mm to 10 mm, in filter chamber of Rain wter tank, over the existing layer of boulders, in required thickness, for all leads & lifts, all complete as per direction of Engineer-in-charge. | 0.15 | Cu.m
(c) | Supplying, filling, spreading & leveling coarse sand of size range 1.5 mm to 2 mm in filter chamber of Rain water tank, in required thickness over gravel layer, for all leads & lifts, all complete as per direction of Engineer -in-charge | 0.1 | Cu.m
SUB HEAD - BUILDING NAME BOARD
63 | Supplying and fixing the name board for the building as per the approved design including the cost of necessary works required for fixing the name board etc. complete | 1 | Each
INTERNAL ELECTRICAL WORKS
64 | Wiring for circuit/submain wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface medium class PVC conduit as required.
| 2 x 1.5 sq.mm + 1 x 1.5 sq.mm earth wire | m | 200
65 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
| 20 mm | m | 200
66 | Supply and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 16
67 | Supplying and fixing following size / modules, PVC box alongwith modular base & cover for modular telephone/ data sockets in recess / surface etc as required.
| 1 or 2 module | Each | 8
68 | Supplying and fixing suitable size PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. | Each | 10
69 | Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 20
70 | Supplying and fixing call bell/buzzer suitable for single phase, 230 volts, complete as required. | Each | 5
71 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface / recessed steel / PVC conduit as required including necessary connectors etc. | m | 200
72 | Supply and fixing TP sheet steel enclosure on surface recess along with 16/25/32/ amps 415V "C" curve TP MCB complete with connections, testing and commissioing etc as required. | Each | 4
73 | Providing and fixing 4mm dia copper wire on surface or in recess for loop earthing as required. | m | 150
74 | Supply and installation of 1x28W flourescent tube fitting, powder coated CRCA steel channel complete with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamp etc complete as required. (Philips TMS122M IxTL-528W EBT / Wipro WIF 90128 SG / GE GET CI 1x28 C/S HF) | Each | 10
75 | Supply and installation of recess mounted type 2x36W CFL cleanroom light fitting with option of rear opening / front opening in robust CRCA housing, glass cover with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamps, mounting chain, hook etc complete as required. (Philips FCS650 2xPL-L36W EBP FOP GT / Wipro WIP 43236 SGA / GE CRP 236CFL BO) | Each | 6
76 | Supply and installation of 1x36W surface mounting mirror optic luminaire with paralite P5 louvers with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamps etc complete as required. (Wipro WVP 45136 SGW / Equi) | Each | 3
77 | Supply and installation of 1x36W recess mounting mirror optic luminaire with paralite P5 louvers with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamps, all mounting accessories etc complete as required. (Wipro WVP 25136 SGW / GE GE CFL 2x18W MOP) | Each | 12
78 | Supply and installation of 2x36W recess mounted direct - indirect downlight luminaire, with translucent acrylic diffuser, powder coated CRCA housing complete with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamp, mounting chain, hook etc complete as required. (Philips FBS580 2xPL-L36W IC OD DF-WH / Wipro WVP 76236 SGA) | Each | 8
79 | Supply & installation of recess mounted 1x18 watts down light fixture, with aluminium reflector, CRCA sheet housing, fresnel lens, complete with all accessories like ballast, 18W CFL lamp etc complete as required. (Wipro WCP 34118 SG / Philips FBH150 M IxPL-C/4P 18W HFM / GE GECCFL1x18 DN) | Each | 16
80 | Supply and installation of 400 mm sweep, wall fan, swinging type with speed control, necessary adapter, of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor all accessories as required complete. (Usha Helix High speed or Equi). | Each | 3
81 | Supply, installation, testing and commissioing of access control system for sterile corridor door and ante room door separately with card controller, door magnetic latch, access card (min 10 nos expandable), cabling between the control and latch including all required accessroies for the proper operation. | Job | 2
82 | Supply, installation, testing & commissioning of LCD Projector with 2100 lumen (lamp mode Standard) with contrast ratio of 3000:1 with a resolution of 1024 X 768, supplied with cordless remote control, VGA cable, ceiling mount kit with all required accessories as required. (Similar to Sony VPL-EX225 or Equ). | Each | 1
83 | Supply & installtaion of pull down screen, High Gain mat white with size 7 ft X 5 ft with all required accessories as required. (Similar to Liberty Grand view or Equ). | Each | 1
84 | Supply and fixing outdoor type polycarbonate enclosure along with 40 amps 415V FP Isolator on surface / recess along with all accessories complete as required. | Each | 3
85 | Supply and fixing FP sheet steel enclosure on surface recess along with 40 amps 415V FP Isolator complete with connections, testing and commissioing etc as required. | Each | 2
86 | Dismantling and re-installing ceiling fan including providing connection etc as required. | Each | 5
87 | Supply, installation, testing and commissioining of IR bullet camera with 3.6mm fixed lens, 700 TV lines, 0.1 lux f 1.2, True day / night vision, with IR distance of 20m. Including all necessary accessories for direct / falseceiling / wall mounting, power adapter for connecting to 230V 50Hz power supply etc complete. | Nos | 5
88 | Supply and installation of 8 channel standalone DVR with H 264 video compression embedded w1 resolution real time recording HDMI and VGA output upto 1920 x 1080 pixel resolution dual stream including all necessary connecting cables, connectors etc as required. | No | 1
89 | Supply and installation of A/V 1TB surveilance hard disk drive including all accessories, connecting cables, connectors etc as required. | Nos | 1
90 | Supply and installation of LCD monitor, 32 inch, full HD, 1920x1080 pixel resolution, contrast ratio 1,00,000:1, with HDMI port, aspect ratio 16:9, including all necessary mounting accessories, connecting cables, connectors etc as required. | Nos | 1
91 | Supply and installation of 6 U wall mounted Network Rack made of steel, powder coated, front glass cover with PDU's, cable manager and cooling fans including all required accessories. | Nos | 1
TOTAL - PART B
GRAND TOTAL (PART A + PART B)