## Internal BOQ
PART G - ELECTRICAL WORKS
S.NO | DESCRIPTION OF ITEM | UNIT | QTY. | RATE | AMOUNT
SCHEDULE ITEMS -PART I
SUB-HEAD - I : INTERNAL WIRING
Note:
Rates of only ISI marked PVC conduit, FR PVC insulated multi-stranded copper conductor single core cables, modular plate type switches and socket outlets in M.S. box of 18 SWG and earth wire have been taken in the following items unless and otherwise specified, only such conduits, cables switches and socket outlets shall be used in the work as per list of approved makes attached with tender documents.
1 | Wiring for Light /Ceiling Fan / Exhaust Fan/ Call Bell point with 1.5 sq.mm FR PVC insulated multi-stranded copper conductor cable in surface / recessed PVC conduit, with modular switch, modular plate, suitable GI box, and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required.
a) | Group -C | Point | 241 | 664 | 160024
2 | Wiring for Light plug 2 x 2.5 sq.mm FR PVC insulated multi-stranded copper conductor, single core cable in recessed ISI marked PVC conduit along with 1 No. 2.5 sq.mm FR PVC insulated copper earth wire for loop earthing as required. | Metre | 90 | 131 | 11790
3 | Wiring for power plug 2 x 4 sq.mm FR PVC insulated multi-stranded copper conductor single core cable in surface / recessed PVC conduit along with 1 No. 4 sq.mm insulated copper earth wire for loop earthing as required. | Metre | 600 | 162 | 97200
4 | Wiring for power plug with 2 x 6 sq.mm FR PVC insulated multi-stranded copper conductor single core cable in surface / recessed PVC conduit along with 1 No. 6 sq.mm FR PVC insulated copper earth wire for loop earthing as required. | Metre | 510 | 206 | 105060
5 | Wiring for power plug with 4 x 6 sq.mm FR PVC insulated multi-stranded copper conductor single core cable in surface / recessed PVC conduit along with 2 Nos. 6 sq.mm PVC insulated solid copper earth wire for loop earthing as required. | Metre | QRO | 358
6 | Supplying and fixing of M.S. box of 18 SWG in recessed including providing and fixing modular plate type 5 pin 6 Amp socket outlet, 6 Amp switch and plug top including connections, an painting etc. as required. (Light Plug). | Each | 18 | 288 | 5184
7 | Supplying and fixing of M.S. box of 18 SWG in recessed including providing and fixing modular plate type Universal 6 pin 16 Amp. Socket outlet, 16 Amp switch and plug top including connections, and painting etc. as required. (Power Plug). | Each | 30 | 366 | 10980
8 | Supplying and fixing of M.S. box of 18 SWG in recessed including providing and fixing modular plate type 5 pin, 6 Amps socket outlet without switch with plug top complete including connections, and painting etc. as required. (Exit / Emergency Light Points). | Each | 4 | 288 | 1152
9 | Wiring for circuit wiring with 2 x 2.5 sq.mm FR PVC insulated multi-stranded copper conductor single core cable with 1 x 2.5 sq.mm. FR PVC inculated earth wire in recessed PVC conduit as required. | Metre | 451.875 | 131 | 59195.625
10 | Wiring for group light points with 2 x 2.5 sq.mm FR PVC insulated multi-stranded copper conductor single core cable in recessed PVC conduit with accessories like junction boxes, bends, socket and connectors including continuous running of 1 No. 2.5 sq.mm FR PVC insulated solid copper conductor earth wire complete with earthing the fixtures and outlet boxes as per specification and drawings (basements, staircase and lift, well light point wiring). | Metre | 50 | 131 | 6550
11 | Providing, fixing, testing and commissioning of under noted rating flush type industrial socket outlet with plug top controlled by ELCB/MCB all mounted in M.S. sheet steel box duly painted in recess / surface complete as required (excluding, wiring and conduit)
a | 20 Amps 3 pin socket outlet controlled by DP MCB. | Each | 15 | 693 | 10395
b | 32A, 3 phase, 5 pin socket outlet controlled by 32A, TPN pole MCB | Each | QRO | 1983
12 | Providing, fixing, testing and commissioning of call bell/buzzer suitable for D.C/A.C, single phase, 230 V, complete as required. | Each | QRO | 54
13 | Supplying and fixing of following sizes of PVC conduit along with the accessories in surface / recess including cutting the wall and making good the same in case of recessed conduit as required as per specification.
a) | 20mm dia PVC conduit | Metre | 1000 | 56.5 | 56500 | 113000
b) | 25mm dia PVC conduit | Metre | 1500 | 64.5 | 96750
c) | 32mm dia PVC conduit | Metre | 1000 | 80.5 | 80500
14 | Wiring for sub mains wiring with following sizes of FR PVC insulated, multi-stranded copper conductor single core cables in surface / recessed PVC conduit as required.
a) | 4 x 6 sq.mm + 2 x 6 sq.mm. earth wire | Metre | QRO | 358
b) | 4 x 10 sq.mm + 2 x 10 sq.mm. earth wire | Metre | 360 | 562 | 202320
c) | 4 x 16 sq.mm + 2 x 16 sq.mm. earth wire | Metre | 50 | 789 | 39450
d) | 4 x 25 sq.mm + 2 x 16 sq.mm. earth wire | Metre | 50 | 789 | 39450
SUBHEAD- II: M.V. PANELS/ DISTRIBUTION BOARD
15 | Supplying, fixing, connecting, testing and commissioning of following way, three poels and neutral, prewired, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete suitable for incomer MCB and RCCB , with loose wire box, terminal blocks, duly prewired qith suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper busbar, netral link, earth bar, din bar, detachable gland, interconnectons, phosphatised and powder coated including earthing etc as required.
A. | 4-way, double door | Nos. | QRO | 6816
B. | 12-way, double door | Nos. | 11 | 12762 | 140382
16 | supplying fixing following rating four pole 415 volts, isolator in existing MCB DB complete with connections, testing and commisioning etc., as required.
A. | 40 amps, c-curve | Nos. | QRO | 554
B. | 63 amps, c-curve | Nos. | 11 | 563 | 6193
17 | supplying fixing following rating four pole 415 volts, four pole (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commisioning etc., as required.
A. | 40 amps | Nos. | QRO | 1703
B. | 63 amps | Nos. | 11 | 1965 | 21615
18 | supplying and fixing 5 amps to 32 amps rating of SP MCB, 240 volts, “C” series, miniature circuit breaker suitable for inductive load in existing MCB DB complete with connections, testing and commissioning etc., s required. | Nos. | 396 | 141 | 55836
SUB-HEAD -III : L.T. CABLES
19 | Supply and making end termination with brass double compression gland including providing and crimping of Aluminium solderless lugs / ferrules for XLPE armoured power Aluminium conductor cable 1.1 KV grade of following sizes:-
a) | 4 x 25 sq.mm | Set | 10 | 192 | 1920
b) | 4 x 16 sq.mm | Set | 12 | 188 | 2256
c) | 4 x 10 sq.mm | Set | QRO | 146
SUB-HEAD -IV : EARTHING
20 | Earthing with GI earth plate 600 x 600 x 6mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement with watering pipe complete with coke and salt etc. as required. | Each | 2 | 3996 | 7992
21 | Supply and fixing of following of copper/GI strip on surface or in recess for connections etc. as required.
a) | 25mm x 5mm GI | Metre | 50 | 120 | 6000
22 | Providing and fixing of 6 SWG GI wire on surface or in recess for loop earthing along with the existing surface/recessed conduit for sub main wiring / cable as required. | Metre | 800 | 19.5 | 15600
SUB HEAD-V : T.V. , TELEPHONE SYSTEM & LAN SYSTEM
23 | Supplying, drawing, connecting and testing of 0.5 mm dia annealed copper conductor PVC insulated PVC sheathed telephone wire in existing conduit/wire way duct etc. as required of following sizes:
a) | 4 Pair (8 core) | Metre | QRO | 24
b) | 2 Pair (4 core) | Metre | 1200 | 15.5 | 18600
24 | Supplying and fixing of following sizes of PVC conduit along with the accessories in surface / recess including cutting the wall and making good the same in case of recessed conduit as required as per specification.
a) | 20mm dia PVC conduit | Metre | 1000 | 56.5 | 56500
b) | 25mm dia PVC conduit | Metre | 200 | 64.5 | 12900
c) | 32mm dia PVC conduit | Metre | 200 | 80.5 | 16100
25 | Supplying and fixing M.S. box with modular type telephone (RJ-11) outlet complete as required. | Each | 30 | 89 | 2670
26 | Supplying and fixing M.S. box with modular type coaxial outlet for TV antenna complete as required. | Each | 3 | 93 | 279
27 | Providing, laying, connecting and testing of unarmoured TV cable RG-6 PVC insulated cable along wall or ceiling or through existing pipe. | Metre | 90 | 22 | 1980
| TOTAL (SCHEDULE PART I) |  |  |  | 1349323.625
NON SCHEDULE ITEMS -PART II
SUB-HEAD - VI : INTERNAL WIRING
28 | Providing, fixing, testing and commissioning of under noted rating flush type industrial socket outlet with plug top controlled by ELCB/MCB all mounted in M.S. sheet steel box duly painted in recess / surface complete as required (excluding, wiring and conduit)
a) | 20 Amps 3 pin socket outlet controlled by DP ELCB (30 mA) | Each | 2 | 2879.8 | 5759.6
SUB-HEAD VII - FANS & LIGHT FIXTURES:
29 | Supplying, fixing, connecting, testing and commissioning of 4x14 watt T-5 light fixture recessed mounting CAT-2 luminaire with 3D lamellae complete with electronic ballast, lockable holders and fluorescent lamp including connection etc. as required similar to Philips Cat no. Xtend TBS669M4xTL514W EBP D6. | Each | 36 | 3734.2138 | 134431.56
30 | Supplying, fixing, connecting, testing and commissioning of 1 x 28 watt T-5 light fixture luminaire complete with electronic ballast, lockable holders and fluorescent lamp including connection etc. as required similar to Philips cat no. Maxlite TCS350 1xTL528W EBE MI | Each | 6 | 698.5025 | 4191
31 | Supplying, fixing, connecting, testing and commissioning of recessed type down-lighter with reflector and louver ,fitting complete with,holder, electronic ballast 1 x 18 W lamp including connections etc. as required similar to Philips Cat no. FBT150 1xPLC/4P18W HFM. | Each | 13 | 1216.025 | 15808.39
32 | Supplying, fixing, connecting, testing and commissioning of recessed type down-lighter with reflector and louver ,fitting complete with,holder, electronic ballast 2 x 18 W lamp including connections etc. as required similar to Philips Cat no. FBH225P 2xPLC/4P18W EBW. | Each | 110 | 1329.6275 | 146259.3
33 | Supplying, fixing, connecting, testing and commissioning of recessed type wall mounted night light fixture complete with , holder, electronic ballast 1 x 10 W lamp including connections etc. as required similar to Anchor. | Each | 10 | 635.39 | 6353.9
34 | Supplying, fixing, connecting, testing and commissioning of surface type light fitting complete with frosted glass cover, , wire guard, holder, electronic ballast 1 x 11 W lamp including connections etc. as required similar to Philips Cat. No. QCZ 805 | Each | 15 | 1998.62 | 29979.3
35 | Supplying, fixing, connecting, testing and commissioning of Bulkhead type light fitting with opal acrylic cover complete with , wire guard, holder, electronic ballast 1 x 11 W lamp including connections etc. as required similar to Philips Cat. No. FXC101 | Each | 6 | 1178.1575 | 7068.96
36 | Supplying, erection, connecting, testing and commissioning of 1200mm sweep ceiling fan complete with blades, down rod, shackle insulator, canopy etc. including providing of electronic step regulator with faceplate matching the existing modular switches as required. | Each | 25 | 1669.749 | 41743.75
37 | Supplying, erection, connecting, testing and commissioning of following size exhaust fan complete with gravity louver and connection with 3 core flexible wire as required.
| a) 305mm 1400 RPM | Each | 6 | 3029.549 | 18177.3
38 | Supplying, fixing, connecting, testing and commissioning of mirror light luminaire with 1 x 13 watt complete with electronic ballast, lamp including connection etc. complete as required similar to Philips cat no. FWZ301 | Each | 6 | 408.185 | 2449.14
39 | Supply, installation, connecting, testing and commissioning of illuminated exit sign with 1 x 8 watt FTL lamp including providing maintenance free batteries & charger capable of working for 2 hr duration mounted on recessed/ ceiling/wall complete with the approved EXIT self adhesive labels as per site requirement as required similar to Prolite cat. PEM 108 E/M RM. | Each | 4 | 6145.1113 | 24580.44
40 | Supply, installation, connecting, testing and commissioning of Motion sensor including all wiring in the existing conduits required similar to Philips cat no. OCCU Switch | Each | 4 | 9083.3 | 36333.2
41 | Supplying and fixing of round shaped fan box fabricated out of 16 SWG sheet steel and 12mm M.S. bar hook duly covered with 3mm thick hylam sheet in white colour of suitable size with C.P. brass screws and making the hole in centre of plate etc. as required. | Each | 25 | 60 | 1500
SUBHEAD- VIII: M.V. PANELS/ DISTRIBUTION BOARD
42 | Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor mounted totally enclosed , extensible on both sides, switch board suitable for use on 415 Volts 3-phase, 4 wire, 50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. (for UPS)
INCOMER:-
1 Nos. 200 Amps. 4P MCCB(25 KA) with electronic releases.
1 Set phase indication lights (R, Y, B)
1 No. Volt Meter (digital type) with inbuilt VSS & control fuses.
1 No. 0-200 Amp. Ammeter (digital type) with inbuilt ASS
BUS BARS:-
200 Amps. 4P Aluminium bus bars (25 KA)
OUT GOINGS:-
| 10 Nos. 100/63 Amps. TPN MCCB(25 KA) with electronic releases. | Set | 1 | 130283.0643 | 130283.0643
43 | Supplying and fixing of non-skid rubber mat 16mm thick and 900mm width as required including cutting to required lengths of approved make with Test Certificates for L.T. panels. | Metre | 20 | 1200 | 24000
44 | Supplying and fixing of fire bucket painted red and duly filled with sand conforming to IS: 2546-1974. | Each | 4 | 250 | 1000
45 | Supplying and fixing of MS stand suitable for supporting two buckets (Pedestal type) | Each | 2 | 1000 | 2000
SUB-HEAD -IX : L.T. CABLES
46 | Supply, laying and testing of under noted sizes of Aluminium conductor XLPE insulated PVC sheathed & sleeved armoured and overall PVC sleeved 1.1 KV grade power distribution cables conforming to relevant IS code and as per specification in ground (in existing trenches) through pipe or on wall / racks cable trays including dressing and clamping the cable with MS zinc passivated clamps etc. as required.
a) | 4 x 25 sq.mm | Metre | 360 | 211.82 | 76255.2
b) | 4 x 16 sq.mm | Metre | 300 | 184.03 | 55209
c) | 4 x 10 sq.mm | Metre | QRO | 169.13
660
47 | Supply and laying of under noted sizes of hume pipe NP-2 grade under the road including 1:3:6 cement concrete bed at 750-1200 depth cutting and making good the same as required as per technical specifications.
a) | 100mm dia | Metre | 20 | 234.55 | 4691
SUB HEAD-X : T.V. , TELEPHONE SYSTEM & LAN SYSTEM
48 | Providing, laying, connecting and testing of multi-core telephone armoured cable of conductor size 0.63mm dia annealed copper conductor PVC insulated PVC sheathed jelly filled (as per DOT specification) cable along wall or ceiling or through existing pipe.
a) | 20 Pair telephone cable | Metre | 200 | 224.9939 | 44998
b) | 5 Pair telephone cable | Metre | QRO | 95.9245
49 | Providing, fixing connecting and testing of under noted size of solderless telephone tag block Krone make in surface/recess in wall required size of M.S. box with hinged lockable cover duly stove enamel painted.
a) | 5 pair tag block | Each | QRO | 1226.417
b) | 30 pair tag block | Each | 2 | 1870.6843 | 3741.36
c) | 200 pair tag block | Each | 1 | 5966.448 | 5966.448
50 | Providing and laying of 80mm dia medium class GI pipe including all fixing accessories concealed or surface as required. | Metre | 20 | 623.4739 | 12469.4
51 | Supplying and fixing M.S. box with Phenolic laminate plate 4- way splitter box for TV antenna complete as required. | Each | 1 | 150 | 150
52 | Supplying and fixing M.S. box with modular type data/ computer (RJ-45) outlet complete as required. | Each | 10 | 354.318 | 3543.2
53 | Providing, laying, connecting and testing of data/ computer Cat-6 cable along wall or ceiling or through existing pipe, including penta scanning documentation etc as required. | Metre | 400 | 11 | 4400
54 | Supplying and fixing of 450 x 450 x 150 M.S. box with Phenolic laminate plate of 16 SWG M.S. Sheet with hinged door cover for mounting TV amplifier including wooden base plate complete as required. | Each | 1 | 500 | 500
SUB HEAD-XI : EXTERNAL LIGHTING
55 | Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor mounted totally enclosed , extensible on both sides, switch board suitable for use on 415 Volts 3-phase, 4 wire, 50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. (Street lighting Panel)
INCOMER:-
1 Nos.100 Amps. TPN MCCB(25 KA) with electronic releases.
1 Set phase indication lights (R, Y, B)
1 No. Volt Meter (digital type) with inbuilt VSS & control fuses.
1 No. 0-200 Amp. Ammeter (digital type) with inbuilt ASS
BUS BARS:-
200 Amps. TP&N Aluminium bus bars (25 KA)
OUT GOINGS:-
8 Nos. 63A TPN, MCB (10KA).
4 Nos. 24 Hr Timer Switch
| 4 Nos. 63A TPN contactor | Set | 1 | 130143.769 | 130143.769
56 | Supplying and fixing in position 11.0 M high steel Single arm tubular poles as per IS-410 SP-54 with 450x450x10mm MS base plate, junction box, internal wiring from junction box to the fixture by 3 x 2.5 Sq.mm FRLS copper wire, pipes for cable entry. The pole to be erected in cement concrete foundation of 1:2:4 and the pole to be powder coated of approved shade etc. as required. along with the Road Lighting Fixture equivalent to Pierlite Cat. No. Approach with 1x150 watt MH lamp. | Each | 5 | 35214.325 | 176071.65
57 | Supply, fixing, testing & commissioning of the Landscaping Lighting Fixture equivalent to Pierlite Cat. No. LED Bollard including 1 no. 3 watt LED lamp of approved shade along with ignitor, necessary brackets, including connections as required. | Each | 20 | 12044.6875 | 240893.8
58 | Supply, fixing, testing & commissioning of the solar lighting Fixture with 1x11 watt CFL light fixture, solar panel, battery banks with maintenance free batteries,timer control switch, mounted on 5M high tubular pole, necessary brackets, including connections as required. | Each | 10 | 35080.75 | 350807.5
59 | Supply, fixing, testing & commissioning of the Gate Lighting Fixture equivalent to Pierlite Cat. No. Vista (graphite) including 1 no. 150 watt MH lamp along with ignitor, necessary brackets, including connections as required. | Each | 2 | 23089.375 | 46178.76
SUBHEAD- XII :SPLIT UNIT AIRCONDITIONERS
60 | Hi Wall Unit
Providing, fixing, testing and commissioning high wall mounted split unit airconditioners with evaporator with fan with motor, cooling coil, filter, all enclosed in decorative plastic casing, condenser with hermatically sealed rotary compressor, condenser coil, propeller fan with motor, cordless remote control, as per standards, requirement and drawings.
a) | 2.0 Tons | Nos. | 2 | 35672 | 71344
61 | Refrigerant Piping
Providing and fixing of copper soft / hard refrigerant piping along (Circuit length) with cable control cabling and earthing shall be insulated with 9 mm thick pipe section of nitrile rubber and finished with nitrile tape, running all pipe as sloted channel, hanger at interval of 2 meters.
| 2.0 TR Hi-Wall Split unit. | Rm | 40 | 657.0993 | 26280
62 | Drain Piping
Supply and installation of PVC drain piping along with U-traps, sockets, hanging supports etc. insulation the same with 6 mm nitrile rubber of density 60 - 80 kg/m3 insulation and finally finished with nitrile tape as per standard and specifications.
a) | 32 mm dia | Rm | 30 | 176.9114 | 5310
b) | 25 mm dia | Rm | 40 | 151.6383 | 6080
| TOTAL (SCHEDULE PART I) |  |  |  | 1896951.9913