## Est Fact 25.07
PART B-ELECTRICAL WORKS
Sl No | Description | Unit | Qty | Rate (Rs. in figures & Words) | Amount
A. LT Wiring
1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required.
1.1 | Group C | Each | 385
2 | Wiring for twin control light point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed steel conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required. | Each | 10
3 | Wiring for circuit/submain wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in surface medium class PVC conduit as required.
a | 2 x 1.5 sq.mm + 1 x 1.5 sq.mm earth wire | m | 2300
b | 2 x 2.5 sq.mm + 1 x 2.5 sq mm earth wire | m | 3600
c | 2 x 4.0 sq.mm + 1 x 4.0 sq mm earth wire | m | 2750
d | 4 x 6 sq. mm + 2 x 6 sq. mm earth wire | m | 500
4 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 20 mm | m | 1800
b | 25 mm | m | 1100
5 | Supplying and drawing 2 pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. | m | 400
6 | Supplying and fixing Telephone socket outlet on the existing modular plate & switch box including connections but excluding modular plate etc. as required. | Each | 20
7 | Supplying and fixing stepped type electronic fan regulator-modular on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 30
8 | Supply and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 80
9 | Supplying and fixing following size / modules, PVC box alongwith modular base & cover for modular telephone/ data sockets in recess / surface etc as required.
a | 1 or 2 module | Each | 30
10 | Supplying and fixing suitable size PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. | Each | 60
11 | Supplying and fixing suitable size PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 30
12 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | Each | 120
13 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, false ceiling with chain and hook including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 300
14 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | Each | 30
15 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
| Upto 450 mm sweep | Each | 25
16 | Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 600
B. MCBs, DBs and Cable Trays
17 | Providing and fixing 100 A, 16kA breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. | Each | 4
18 | Supplying and fixing following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, with provision of 100 amps TP 16 KA MCCB as incomer, interconnection between incomer MCCB and bus bars (but without MCB's/ MCCB) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
a | 4 Way TP | Each | 2
b | 8 Way TP | Each | 2
19 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
a | 8 way, Double door | Each | 2
b | 12 way, Double door | Each | 2
20 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
a | 6 way, Double door | Each | 3
b | 8 way, Double door | Each | 3
21 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
a | 4 way, Double door | Each | 4
b | 6 way, Double door | Each | 6
c | 8 way, Double door | Each | 6
22 | Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 40 amps | Each | 2
b | 63 amps | Each | 2
23 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 40 amps | Each | 8
b | 63 amps | Each | 12
24 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 25 amps | Each | 5
b | 40 amps | Each | 3
c | 63 amps | Each | 2
25 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 25 amps | Each | 8
b | 40 amps | Each | 8
c | 63 amps | Each | 12
26 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | Single pole | Each | 270
b | Double pole | Each | 15
c | Triple pole | Each | 40
d | Triple pole and neutral | Each | 60
27 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 200
28 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32amps 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | Each | 15
29 | Supply and fixing TP sheet steel enclosure on surface recess along with 16/25/32/ amps 415V "C" curve TP MCB complete with connections, testing and commissioing etc as required. | Each | 25
30 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 25
31 | Supplying and fixing 30 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 30 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 10
32 | Supply and installing following size of perforated GI cable trays with perforations not more than 17.5% in convenient sections, joined with connectors, GI suspenders including nuts and bolts, bends, tees etc as required
a | 150mm x 50 mm depth x 1.6mm thick | m | 300
b | 300mm x 50 mm depth x 1.6mm thick | m | 600
C. Earthing & Lightning protection
33 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | Each | 10
34 | Earthing with GI earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Each | 8
35 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | m | 800
36 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | m | 100
37 | Providing and fixing 8 SWG dia G.I. wire on surface or in recess for loop earthing as required. | m | 800
38 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For horizontal run) | m | 300
39 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For vertical run) | m | 300
40 | Providing and fixing testing joint, made of 20 mm X 3 mm thick G.I. strip, 125 mm long, with 4 nos. of G.I. bolts, nuts, chuck nuts and spring washers etc. complete as required. | Each | 10
41 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrode directly in ground as required. | m | 300
D. MV Cable laying and Termination
42 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
a | Upto 35 sq. mm | m | 70
b | Above 35 sq. mm and upto 95 sq. mm | m | 80
c | Above 95 sq. mm and upto 185 sq. mm | m | 50
43 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 280
b | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | m | 150
c | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | m | 30
44 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
a | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 100
b | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | m | 120
c | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | m | 70
45 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | Each | 30
46 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a | 3.5 x 95 sqmm cable | Each | 2
b | 3.5 x 70 sqmm cable | Each | 4
c | 3.5 x 50 sqmm cable | Each | 8
d | 3.5 x 35 sqmm cable | Each | 16
e | 3.5 x 25 sqmm cable | Each | 8
f | 4 x 16 sqmm cable | Each | 16
g | 4 x 10 sqmm cable | Each | 6
h | 4 x 6 sqmm cable | Each | 6
47 | Providing, laying and fixing of 100mm dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required | m | 50
48 | Providing, laying and fixing of 150 mm dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. | m | 20
E. LT Cables
49 | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date.
a | 3.5 x 95 sqmm cable | m | 140
b | 3.5 x 70 sqmm cable | m | 280
c | 3.5 x 50 sqmm cable | m | 180
d | 3.5 x 35 sqmm cable | m | 500
e | 3.5 x 25 sqmm cable | m | 400
f | 4 x 16 sqmm cable | m | 500
g | 4 x 10 sqmm cable | m | 400
h | 4 x 6 sqmm cable | m | 100
F. Light Fixtures
50 | Supply of 1x28W flourescent tube fitting, powder coated CRCA steel channel complete with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamp etc complete as required. (Philips TMS122M IxTL-5-28W EBT / Wipro WIF 90128 SG / GE GET CI 1x28 C/S HF) | Each | 40
51 | Supply and installation of 2x36W recess mounted direct - indirect downlight luminaire, with translucent acrylic diffuser, powder coated CRCA housing complete with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamp, mounting chain, hook etc complete as required. (Philips FBS580 2xPL-L36W IC OD DF-WH / Wipro WVP 76236 SGA) | Each | 10
52 | Supply and installation of recess mounted type 2x36W CFL cleanroom light fitting with option of rear opening / front opening in robust CRCA housing, glass cover with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamps, mounting chain, hook etc complete as required. (Philips FCS650 2xPL-L36W EBP FOP GT / Wipro WIP 43236 SGA / GE CRP 236CFL BO) | Each | 10
53 | Supply of 4x28W surface mounting luminaire with reflectors, closed version with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamps etc complete as required. (Wipro WHF 30428 SGW / Philips TPS325 4xTL-5-28W EBP) | Each | 120
54 | Supply & installation of recess mounted 1x18 watts down light fixture, with aluminium reflector, CRCA sheet housing, fresnel lens, complete with all accessories like ballast, 18W CFL lamp etc complete as required. (Wipro WCP 34118 SG / Philips FBH150 M IxPL-C/4P 18W HFM / GE GECCFL1x18 DN) | Each | 10
55 | Supply of 1x18W surface mounted luminaire with opal acrylic diffuser complete with all electrical accessories like electronic ballast, lamp holder, 18W T8 lamps etc. complete with all mounting accessories etc as required. (Philips TMS520/ 118 / Wipro WRF 21118 / GE TRI 118) | Each | 10
56 | Supply of 1x28W flourescent tube fitting, clear polycarbonate housing, SS toggles, dust and moisture proof (IP66) complete with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamp etc complete as required. (Philips TCW450 IxTL-528W EBT / Wipro WIF 83128 SGA / GE MAR 128 FTL HF) | Each | 20
57 | Supply of 2x28W flourescent tube fitting, clear polycarbonate housing, SS toggles, dust and moisture proof (IP66) complete with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamp etc complete as required. (Philips TCW450 2xTL-528W EBT / Wipro WIF 83228 SGA / GE MAR 228 FTL HF) | Each | 20
58 | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod,suspension shackle,canopy etc with out regulator complete with all accessories as required. ( Usha Sonata max / Crompton High Breeze) | Each | 40
59 | Supply and installation of 400 mm sweep, wall fan, swinging type with speed control, necessary adapter, of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor all accessories as required complete. (Usha Helix High speed or Equi). | Each | 15
60 | Supply of heavy duty exhaust fan 450 mm sweep, 900 rpm, metal blades of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor and all accessories as required complete. | Each | 15
61 | Supply of 250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/shutters and all accessories as required complete. (Make : Usha Crisp Air or equivalent) | Each | 5
62 | Supply and installation of IP65,70W MH street light luminaire, with die cast aluminium housing, POT optics, toughened glass, stainless steel toggle, heavy duty copper ballast, pf capacitor, 1x70W MH lamp etc as required. The light fitting shall be suitabily installed with GI pipe and all required accessories to outside wall of building. The item shall include 3C x 1.5 sqmm PVC insulated copper unarmoured cable for connecting between the luminiare and the junction box. (Similar to Philips CRP320 IxCDMTT70W FG TS or equivalent). | Nos | 15
G. Panels and Telephone system
63 | Supply, Installation, Testing & Commissioning of Lighting panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, free standing, floor mounting, dust and vermin proof, powder coated, outdoor type, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
160A, TPN, switch disconnector unit (Isolator), AC23, 415V, 50Hz, complete with handle assembly having door interlock - 1 no.
Busbar
1 Set of 200 A TPN busbars of high conductivity electrolytic quality Aluminium alloy.
Instruments
2A, C curve SP MCB - 3 nos.
RYB indication lamp, LED type - 3 nos.
1 No 3 phase Digital Multi function meter to read V, A, F Acc class 1.
150/5A 5VA class 1 resin cast CT - 1 set
1 No 3 phase 4 wire CT operated energy meter, 5-10 A, Acc. Class 1.
Outgoing.
63A TPN C curve MCB - 8 nos.
| 32A TPN C curve MCB - 2 nos. | Each | 1
64 | Supply, Installation, Testing & Commissioning of Power panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, free standing, floor mounting, dust and vermin proof, powder coated, outdoor type, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
250A, TPN, switch disconnector unit (Isolator), AC23, 415V, 50Hz, complete with handle assembly having door interlock - 1 no.
Busbar
1 Set of 300 A TPN busbars of high conductivity electrolytic quality Aluminium alloy.
Instruments
2A, C curve SP MCB - 3 nos.
RYB indication lamp, LED type - 3 nos.
1 No 3 phase Digital Multi function meter to read V, A, F Acc class 1.
250/5A 5VA class 1 resin cast CT - 1 set
1 No 3 phase 4 wire CT operated energy meter, 5-10 A, Acc. Class 1.
Outgoing.
100A, 16kA, TP+NL MCCB having adjustable thermal magnetic release for O/L & SC protection - 3 nos.
| 63A TPN C curve MCB - 6 nos. | Each | 1
65 | Supply, fabrication and installation of structural steel work fixed with or without connecting plate, including cutting, hoisting, fixing in position, bolting / welding in built up sections, and applying 2 coat of steel primer and 2 coat of approved shade paint for the support of cable tray, panels etc complete with all required accessories like anchor bolt, nut bolt, easher etc complete. | kg | 1800
66 | Supplying and fixing following rating, 415 Volts, "C" series, miniature circuit breaker suitable for power loads of following poles in the existing MCB DB complete with connections, testing and commissioning etc as required.
a | 40A TP MCB | Each | 10
b | 63A TP MCB | Each | 18
67 | Supply and fixing FP sheet steel enclosure on surface recess along with 40 amps 415V FP Isolator complete with connections, testing and commissioing etc as required. | Each | 10
68 | Supply and Installation of 20 pair MDF box, back mount frame and original krone connectors with all accessories. | Each | 5
69 | Supply and Installation of 10 pair MDF box, back mount frame and original krone connectors with all accessories. | Each | 5
70 | Supply & fixing modular type computer outlet (RJ-45) with modular base and cover plate, GI box complete with all accessories, connection etc. complete as required. | Each | 25
71 | Supply and laying 4 pair CAT 6 UTP cable in the exisitng surface / recessed steel / PVC conduit as required. | m | 500
72 | Supply and laying 20 pair 0.5 sqmm FR PVC insulated annealed copper conductor, jelly filled armoured telephone cable in surface / through pipe / underground including excavation and re-filling including all accessories as required. | m | 50
H. Miscellaneous
73 | Supply and providing 6 mm thick & 1 m wide electrical grade chequered type rubber mat to withstand 3.3 KV dielectric strength conforming to IS 5429/ 1969. | m | 20
74 | Liasoning works and obtain statutory approval from Electricity Board, Electrical inspectorate and any another body for the successful energisation of electrical supply to the building. All necessary drawings and documents required for the same has to be prepared and submitted by the Contractor with the concurrence and approval of the Engineer-in-charge. | Job | 1
TOTAL (PART B- ELECTRICAL WORKS)
GRAND TOTAL (PART A+ PART B)