## TENDER FOR SUPPLY OF 40 KVA DIESEL GENERATOR SET ## FOR ART-IVF PROJECT IN IMCH, KOZHIKODE ### IFB NO: HLL/AFT/TDG/IVF/Equip/2014-15/IV ##### HLL LIFECARE LIMITED (A GOVT. OF INDIA ENTERPRISE) AKKULAM FACTORY, SREEKARIAM P.O. THIRUVANANTHAPURAM – 17 Phone +91 471 244 5930, Fax +91 471 244 5935 Email: tradingpaft@lifecarehll.com Web: www.lifecarehll.com

##### HLL LIFECARE LIMITED

(Formerly Hindustan Latex Limited)

AKKULAM  FACTORY,   SREEKARIAM  P.O.  THIRUVANANTHAPURAM - 17

## Tender for Supply of 40 KVA Diesel Generator Set

BID REFERENCE	            : IFB NO: HLL/AFT/TDG/IVF/EQUIP/2014-15/IV					                                             Dt.25/11/2014

DATE OF COMMENCEMENT

OF SALE OF BIDDING DOCUMENT	:	25/11/2014

LAST DATE FOR SALE OF BIDDING

DOCUMENT					:	15/12/2014   ,     	11.30 HRS

LAST DATE AND TIME FOR

RECEIPT OF BIDS				:	15/12/2014  ,     	14.00 HRS

TIME AND DATE OF OPENING

OF BIDS					:	15/12/2014  ,     	15.30 HRS

PLACE OF OPENING OF BIDS		:	HLL LIFECARE LIMITED

AKKULAM  FACTORY,

SREEKARIAM  P.O.

THIRUVANANTHAPURAM – 17

Phone +91 471 244 5930

Fax      +91 471 244 5935

Email: tradingpaft@lifecarehll.com

ADDRESS FOR COMMUNICATION		:	Joint General Manager (Materials)

HLL LIFECARE LIMITED

AKKULAM  FACTORY,

SREEKARIAM  P.O.

THIRUVANANTHAPURAM – 17

Phone +91 471 244 5930

Fax      +91 471 244 5935

Email: tradingpaft@lifecarehll.com

ABSTRACT

SECTION No.		DESCRIPTION	                                  PAGE No.

PART  A

SECTION I		INVITATION FOR BIDS (IFB)				    04

SECTION II		INSTRUCTION TO BIDDERS (ITB)				    08

SECTION III		GENERAL CONDITIONS OF CONTRACT (GCC)		    18

SECTION IV		SPECIAL CONDITIONS OF CONTRACT (SCC)	                24

SECTION V		TECHNICAL SPECIFICATIONS 				    28

SECTION VI		QUALIFICATION CRITERIA					    62

SECTION VII		PROFORMA FOR EQUIPMENT AND QUALITY CONTROL   63

SECTION VIII		PERFORMANCE STATEMENT				    64

PART : B

SECTION IX		PRICE BID FORM						    67

SECTION X		PRICE SCHEDULE (I)					    68

SECTION XI		AMC PRICE SCHEDULE (I)					    76

SECTION XII		CHECK LIST							    89

Section XIII           	 Bank Guarantee Form for EMD                                               77

Section XIV     	Manufacturer‟s Authorisation Form                                         78

Section XV           Bank Guarantee Form for Performance Security /CMC Security  79

Section XVI            Proforma of Consignee Receipt Certificate  (Issue Note)           82

Section XVII           Proforma of Final Acceptance Certificate by the Consignee        83

Section XVIII           Consignee details

## PART - A

SECTION I

INVITATION FOR BIDS (IFB)

HLL LIFECARE LIMITED

AKKULAM FACTORY, SREEKAYAM

THIRUVANANTHAPURAM - 17

INVITATION FOR BIDS (IFB)

IFB NO: HLL/AFT/TDG/IVF/Equip/2014-15/IV

HLL Lifecare Limited hereby invites sealed bids under TWO-BID system from eligible  bidders for  supply, installation and commissioning of 40 KVA Diesel Generator Set at IMCH, Medical College Hospital, Kozhikode, Kerala.

| Sl.No. | DESCRIPTION OF EQUIPMENT | Qty | EMD (Rs): |
| --- | --- | --- | --- |
| 1 | Diesel Generator Set - 40 KVA | 1 | 10000.00 |

Sealed Tenders will be accepted till 14.00 Hrs on 15/12/2014,

1. Interested eligible Bidders may obtain further information from the office of the Joint General Manager (Materials), HLL Lifecare Ltd, Akkulam Factory, Thiruvananthapuram -17

2.  Deleted.

3. The Tender Document can be downloaded from our Website www.lifecarehll.com.

4. Interested eligible bidders may submit their bidding documents to the office of the Joint General Manager (Materials), HLL Lifecare Ltd, Akkulam Factory, Thiruvananthapuram –17 on the specified date and time.

5. The bids must be accompanied by the documents specified herein and must be delivered to the office of Joint General Manager (Mtls) on or before 15/12/2014,      14.00 Hrs. The Technical Bids will be opened on 15/12/2014, at 15.30 Hrs, in the presence of the bidders or their duly authorized representatives who wish to attend the bid opening on the specified date and time at HLL's office mentioned above. In the event of the date being declared is a closed holiday for HLL, the due date for submission of bids and opening of bids will be the following working day at the

appointed time.

SECTION II

INSTRUCTIONS TO BIDDERS

INSTRUCTION TO BIDDERS

A. INTRODUCTION

1. Eligible Bidders

  - Eligible to participate in the tender:

| Sl. No. | Minimum Eligibility criteria | Narrations |
| --- | --- | --- |
| 1 | Experience | Should have a minimum 3 years’ experience in the field of supply, installation and commissioning of Diesel Generator Sets of 40 KVA or higher capacity. |
| 2 | Licenses/Registrations for undertaking, supply and installation contracts | - Primary manufactures who participate in the tender must produce their valid manufacturing license. - Item wise Technical compliance sheet to match the technical specification prescribed in this tender. - Tenderers, other than manufacturers, who participate in this tender must produce the follows: - An authorization letter from Manufacturers / authorized distributors to participate in this tender. - Manufacturer’s manufacturing license / Distributor appointment letter. |
| 3 | Quality Certifications | 1) Should have necessary valid Quality / System Certifications like ISO, CE, FDA etc) as applicable – to match technical specifications/requirements as in the tender |
| 4 | Good financial capability necessary to perform the Contract | - Annual Turn over Statement preceding last three years (Certified by the Chartered accountant) - Profit & Loss Account for preceding last three years (Certified by the Chartered accountant) - Balance sheet for the past preceding last three years (Certified by the Chartered accountant) |

1.2 	Bidders should not be associated with the purchaser for the preparation 	of the design, specifications, and other documents used for the 	procurement of the equipments under this Invitation for Bids.

1.3 	Deleted.

1.4 	Deleted.

2. Cost of Bidding

2.1 	The Bidder shall bear all costs associated with the preparation and submission of its bid and HLL Lifecare Limited, Akkulam Factory, Thiruvananthapuram hereinafter referred to as “the Purchaser”, will in no case be responsible or liable for these costs, regardless of the conduct or outcome of the bidding process.

B. THE BIDDING DOCUMENTS

3. Contents of Bidding Documents

3.1 	The equipment required, bidding procedures and contract terms are prescribed in the Bidding documents. In addition to the Invitation for Bids, the Bidding documents include:

a.	Instruction to Bidders (ITB);

b.	General Conditions of Contract (GCC);

c.	Special Conditions of Contract (SCC);

d.	Technical Specifications;

e. 	Qualification criteria;

f.	Performance statement

g.	Bid Form;

h.	Price Schedule;

i.	Check List

3.2 	The Bidder is expected to examine all instructions, forms, terms and specifications in the Bidding Documents. Failure to furnish all information required by the Bidding Documents or submission of a bid not substantially responsive to the Bidding Documents in every respect will be at the Bidder’s risk and may result in rejection of its bid.

4. Clarification of Bidding Documents

4.1  	A prospective Bidder requiring any clarification of the Bidding Documents may notify the Purchaser in writing at the Purchaser’s mailing address indicated in the Invitation for Bids. The Purchaser will respond in writing to any request for clarification of the Bidding Documents which it receives not later than 7 days prior to the deadline for submission of bids prescribed by the Purchaser. Any such response (relevant) against the clarification of the supplier shall be notified in our website only.

5. Amendment of Bidding Documents

5.1  	At any time prior to the deadline for submission of bids, the Purchaser may, for any reason, whether at its own initiative or in response to a clarification requested by a prospective bidder, modify the Bidding Documents by an amendment.

Those bidders who download the tender documents from our website should furnish the Name and address of the vendor, name of contact person, telephone numbers and Email details immediately by Email to HLL Akkulam. Any changes pertains to this tender shall be communicated only through our website www.lifecarehll.com

5.2 	All prospective bidders who have received the Bidding Documents will be notified of the amendment in writing or by mail and will be binding on them.

5.3 	In order to allow the prospective bidders reasonable time in which to take the amendment into account in preparing their bid, the Purchaser may, at its discretion, extend the deadline for the submission of bids

C. PREPARATION OF BIDS

6. Language of Bid

6.1    The Bid prepared by the bidder and all correspondence and documents relating to the bid exchanged by the Bidder and the Purchaser, shall be written in  English language. Supporting documents and printed literature furnished by the Bidder may be written in another language provided they are accompanied by an accurate translation of the relevant passages in English language in which case, for purposes of interpretation of the Bid, the English translation shall govern

7. Documents Comprising the Bid

Following documents and forms are to be included in the Techno Commercial bid and Price bid respectively.

7.1 TECHNICAL BID

The technical bid shall consist of the following documents.

- Tender Fee : DD for Rs. 500.00 (inclusive of tax) drawn in favour of HLL Lifecare Limited payable at Thiruvananthapuram is to be attached towards tender fee.

- EMD / Bid Security for Rs. 10,000.00 in the form of DD, drawn in favor of HLL Lifecare Limited, payable a Thiruvananthapuram. The EMD / Bid Security shall be refunded to the non-responsive bidders within 60 days from the date of opening of Bid. The Tender received without EMD will be rejected.

- The technical specifications enclosed along with the bid document shall be confirmed by signature of the bidder/authorized signatory of the bidding firm, in all pages and authorized by official seal. The information shall be filled, wherever necessary as per the instructions given.

- Duly attested copies of factory license/Industrial licenses, sales tax registration, and documents to prove the legal status, place of registration and principal place of business of the bidding firm.

- Duly attested copies of quality certificates for the product, quality system certifications as specified in the technical specification. Item wise Product catalogue/Detailed printed literature to prove the technical specification along with COMPLIANCE SHEET to each point confirming to technical specification should be attached with offer.

- Copy of Balance sheet for the last three financial years, duly certified by a chartered accountant.

- Performa for equipment and quality control, duly filled as per section VII

- Performance statement in the proforma under section VIII

- Documentary evidence established in accordance with ITB Clause 1 that the Bidder is eligible to bid and is qualified to perform the contract if its bid is accepted;

- Documentary evidence established in accordance with ITB Clause 12 that the equipment and ancillary services to be supplied by the Bidder shall conform to the Bidding Documents

- Duly filled Check list as per section XII

7.2  PRICE BID

Duly filled Bid Form and Price Schedule as per Sections IX, X(I), X(II) and XI respectively.

a). The Tenderer shall indicate on the Price Schedule SECTION X(I), all the specified components of prices shown therein including the 	unit prices and total tender prices of the goods and services it proposes to supply against the requirement.

b) The cost of consumable like Engine Oil, Filter, and battery water etc. actually to be paid by the Purchaser/Consignee at the destination, during preventive maintenance in Warranty period, shall be specifically mentioned by the Bidder in the Price Schedule SECTION X(II). Such costs of consumables incurred by supplier/ their agencies shall be reimbursed by Purchaser/HLL to the supplier on submission of bills by the supplier to this effect with original bills of consumables after each preventive maintenance.

c) All the columns shown in the price schedule should be filled up as required. If any column does not apply to a tenderer, same should be clarified as “NA” by the tenderer.

d) All sundry equipments, fittings, units assemblies, accessories and all other items which are useful and necessary for efficient assembly and installation of equipment and components of the supply/work be deemed to have been included in the tender irrespective of the fact whether such items are specifically mentioned in the tender documents or not.

e) While filling up the columns of the Price Schedule, the following aspects should be noted for compliance:

i)) All kind of taxes and duties including Sales Taxes and Excise Duties, 		levies including work contract taxes  etc. which will be payable on the 		goods if the contract is awarded;

ii) Charges towards Packing & Forwarding, Inland Transportation, 			Insurance (local transportation) would be borne by the Contractor from 		warehouse to the project site including Loading/Unloading, 	and other 		local costs incidental to delivery of the goods at the destination,  			installation, testing commissioning at site and clearance from local 			authorities etc.

iii) The price of Incidental Services, as mentioned in requirements and 		Price Schedule;

iv).The prices of Turnkey (if any), as mentioned in requirements,   Technical Specification and Price Schedule;

v) The rates quoted by the tenderer, shall be firm and fixed.

vi)The price of Annual CMC, as mentioned in requirements, Technical 		Specification and Price Schedule.

8. Bid Form

8.1 	The Bidder shall fill up the Bid Form and the appropriate Price Schedule furnished in the bidding documents, indicating, a brief description of the equipment, its country of origin etc.

9.  Bid Prices

9.1    The Bidder shall indicate in the Price Schedule the unit prices and total Bid prices of the equipment it proposes to supply under the Contract.

10. Bid Currencies

10.1 Prices shall be quoted in Indian Rupees.

11. Documents establishing bidder’s eligibility and qualifications

11.1 	Pursuant to ITB Clause 7, the bidder shall furnish, as part of its bid, documents establishing the bidder’s eligibility to bid and its qualifications to perform the Contract if its bid is accepted.

11.2 	The documentary evidence of the Bidder’s qualifications to perform the Contract if its bid is accepted, shall establish to the HLL’s satisfactions.

(a) that the bidder has the financial, technical and execution capability necessary to perform the Contract and meets the criteria outlined in the qualification requirements specified in Section VI. To this end, all bids submitted shall include the following information.

(i) The legal status, place of registration and principle place of business of the company or firm or partnership, etc;

(ii) Details of experience and past performance of the bidder on item offered and on those of similar nature for the last Three years and details of current contracts in hand and other commitments (as per proforma given in Section VIII)

12 .Documents establishing equipment’s conformity to bidding documents

12.1 	Pursuant to ITB Clause 7, the Bidder shall furnish, documents establishing the conformity to the bidding documents of equipment and services which the bidder proposes to supply under the contract.

12.2   Deleted

12.3  Deleted

13. Period of Validity of Bids

13.1  Price Bid shall be valid for One year from the date of opening of Price Bid

13.2 	In exceptional circumstances, the Purchaser may solicit the bidders consent to an extension of the period of validity. The request and the responses thereto shall be made in writing.

14. Format and Signing of Bid

14.1 	The bidder shall prepare the bid clearly marking each “Technical Bid” and “Price Bid” as appropriate.

14.2   The bid shall be typed or written in indelible ink and shall be signed by the Bidder or a person or persons duly authorized to bind the Bidder to the Contract. The letter of authorization shall be indicated by written power-of-attorney accompanying the bid. All pages of the bid, except for unamended printed literature, shall be initialed by the person or persons signing the bid.

14.3  Any interlineations, erasures or overwriting shall be valid only if they are initialed by the person or persons signing the bid. The bid with interlineation, erasures or overwriting not accordingly initialed shall be considered invalid.

D. SUBMISSION OF BIDS

#### 15. Sealing and Marking of bids

Separate bids shall be submitted for Technical and Price bids.

15.1   The bidders shall seal Technical bid   and Price bid separately duly super-scribing the envelopes as “TECHNICAL BID” - cover “A” and “PRICE BID” - cover “B” on each envelop.  Then the both envelopes (cover “A” & cover “B”) shall put and seal in an outer envelope, which shall be super-scribed with Tender No & “Tender for DG Sets 40 KVA for ART IVF Unit”

15.2   The inner and outer envelopes shall be addressed to the Purchaser at the following address:

Joint General Manager (Materials)

HLL Lifecare Limited, Akkulam Factory, Sreekaryam  P.O. ,

Thiruvananthapuram -17, Kerala   Phone 0471 2445930 / 2445935

Email :tradingpaft@lifecarehll.com

(a) The outer envelope shall bear the Invitation for Bids (IFB) number, and a 	statement. “DO NOT OPEN BEFORE” 14.30 Hrs. ON 15/12/2014”

(b) The inner envelope shall also indicate the name and address of the bidder 	to enable the bid to be returned unopened in case it is declared 	“late / 	disqualified”.

(c) If the inner and outer envelopes are not sealed and marked as required, the Purchaser will assume no responsibility for the bid’s misplacement or premature opening.

- Bids must be received by the Purchaser at the address specified not later than the date and time specified in the Invitation For Bid.  In the event of the specified date for the submission of bids, being declared a holiday for the Purchaser, the bids will be received up to the appointed time on the next working day.

- The Purchaser may, at its discretion, extend this deadline for the submission of bids by amending the bidding documents in which case all rights and obligations of the Purchaser and bidders previously subject to the deadline will thereafter be subject to the deadline as extended.

16. LATE BIDS

16.1   Any bid received by the Purchaser after the deadline for submission of bids prescribed by the Purchaser, will be rejected and returned unopened to the bidder.

17.  MODIFICATION AND WITHDRAWAL OF BIDS

17.1 	The bidder may modify or withdraw its bid after the bid submission, provided that written notice of the modification or withdrawal is received by the Purchaser prior to the deadline prescribed for submission of bids.

17.2  The bidder’s modification or withdrawal notice shall be prepared, sealed, marked and dispatched in accordance with the provisions of ITB Clause 15.  A withdrawal notice may also be sent by email, but followed by a signed confirmation copy, post-marked not later than the deadline for submission of bids.

17.3   No bid may be modified subsequent to the deadline for submission of bids.

17.4 	No bid may be withdrawn in the interval between the deadline for submission of bids and the expiration of the period of bid validity specified by the bidder in the Bid Document.

E. BID OPENING AND EVALUATION

18. Opening of Bids by Purchaser

18.1 The Purchaser will open all technical bids (Cover A), in the presence of bidder's representatives who choose to attend, at 14.30 Hrs on 15/12/2014    at the following location/Office of:

Joint General Manager (Materials)

HLL Lifecare Limited, Akkulam Factory, Sreekaryam  P.O. ,

Thiruvananthapuram -17  Phone 0471 2445930 / 2445935

Email : tradingpaft@lifecarehll.com

18.2 	The bidder’s representatives who are present in bid opening shall sign in a register evidencing their attendance. In the event of the specified date of bid opening being declared a holiday for the Purchaser, the bids shall be opened at the appointed time and location on the next working day.

18.3   The bidder’s names, modifications, bid withdrawals and such other details as the Purchaser, at its discretion, may consider appropriate will be announced at the opening. No bid shall be rejected at bid opening, except for late bids, which shall be returned unopened to the bidder pursuant to ITB Clause 16.

18.4    Deleted

18.5   The “Price Bid” (Cover B) will be opened after evaluation of “Technical bids” (Cover A) and the date and time will be intimated to bidders whose bids are technically qualified and responsive.

18.5 	The purchaser will scrutinize the technical bid for compliance to the specifications and documentation requirement as per the bid document. Purchaser will depute its competent officers to the premises of the bidders qualified on the basis of technical scrutiny, for on-site evaluation of the claims made in the technical bid, if deemed appropriate on purchaser’s sole discretion. The bidders will be short-listed on the basis of responsiveness of technical bid as well as report of on-site technical evaluation. The price bid of the bidders who are disqualified at the technical scrutiny and on-site evaluation will be returned un-opened. The on-site evaluation may include the inspection of the specimen sample of the equipment. The short listed bidders will be informed about the time, date and venue of the price bid opening. The successful bidder shall be identified on the basis of lowest evaluated substantially responsive bid.

19.  CLARIFICATION OF BIDS

19.1   During evaluation of bids, the Purchaser may, at its discretion, ask the bidder for a clarification of its bid.  The request for clarification and the response shall be in writing and no change in prices or substance of the bid shall be sought, offered or permitted.

20   PRELIMINARY EXAMINATION

  - The Purchaser will examine the bids to determine whether they are complete, whether any computational errors have been made, whether the documents have been properly signed, and whether the bids are generally in order.

20.2  Arithmetical errors will be rectified on the following basis.  If there is a discrepancy between the unit price and the total price that is obtained by multiplying the unit price and quantity, the unit price shall prevail and the total price shall be corrected. If there is a discrepancy between words and figures, the amount in words will prevail.  If the bidder does not accept the correction of the errors, its bid will be rejected.

20.3 	The Purchaser may waive any minor informality or non-conformity or irregularity in a bid, which does not constitute a material deviation, provided such a waiver does not prejudice or affect the relative ranking of any bidder.

20.4   	Prior to the detailed evaluation, pursuant to Clause ITB 21, the purchaser will determine the substantial responsiveness of each bid to the bidding documents. For purposes of these clauses a substantially responsive bid is one which conforms to all the terms and conditions of the bidding documents without material deviations. Deviations from or objections or reservations to critical provisions such as those concerning Warranty, Force Majeure, Applicable law  and Taxes and Duties  will be deemed to be material deviation. The purchaser’s determination of a bid’s responsiveness is to be based on the contents of the bid itself without recourse to extrinsic evidence.

20.5   If a bid is not substantially responsive, it will be rejected by the Purchaser and may not subsequently be made responsive by the bidder by correction of the non-conformity.

21. EVALUATION AND COMPARISON OF BIDS

21.1  The Purchaser will evaluate and compare bids previously determined to be substantially responsive, pursuant to ITB Clause 20.

21.2   The purchaser’s evaluation of a bid will take into account the bid price including all costs as well as duties and taxes paid or payable and price of incidental services, if any, in the manner and to the extent indicated in ITB Clause 21.3 and in the technical specifications and as following:

i.  cost of transportation, insurance and other costs incidental to the delivery of goods; to designated delivery destination and installation and handing over the same to the Purchaser, at IMCH, Medical College Hospital, Kozhikode.

ii. Deleted

21.3 	Pursuant to ITB Clause 21.2 the following evaluation methods will be applied:

(a) transportation from factory, insurance and   incidentals.

(i)  transportation, insurance and other incidentals, for delivery of goods to the required locations mentioned in ITB Section 21.2. The above costs will also be considered in the bid price.

(b)  Spare parts and after sales service facilities:

The cost of the Purchaser of establishing the minimum service facilities and parts inventories, as outlined elsewhere in the bid invitation, if quoted separately, shall be added to the bid price.

(c) Annual Comprehensive Maintenance Contract (CMC)

The Purchaser desires to have separately annual comprehensive maintenance charges for a period of 7 years after the expiry of warranty period of 2 years, clearly indicating year wise comprehensive maintenance charges, as per Section XI.

22. CONTACTING THE PURCHASER

22.1      No bidder shall contact the Purchaser on any matter relating to its bid, from the time of the bid opening to the time the contract is awarded.    If the bidder wishes to bring additional information to the notice of the purchaser it should do so in writing.

22.2    Any effort by a bidder to influence the purchaser in its decisions on bid evaluation, bid comparison, or selection may result in the rejection of the bidders bid.

F. AWARD OF CONTRACT

23. POST QUALIFICATION

23.1 	In the absence of pre-qualification, the Purchaser will determine to its satisfaction whether the bidder that is selected as having submitted the lowest evaluated responsive bid meets the criteria specified in ITB Clause 11.2 and is qualified to perform the contract satisfactorily

23.2 	The determination will take into account the bidders financial, technical and production/other capabilities. It will be based upon an examination of the documentary evidence of the bidder’s qualifications submitted by the bidder, pursuant to ITB Clause 11 as well as such other information as the Purchaser deems necessary and appropriate.

23.3 	An affirmative determination will be a prerequisite for award of the contract to the bidder. A negative determination will result in rejection of the bidders bid, in which event the Purchaser will proceed to the next lowest evaluated bid to make a similar determination of that bidder’s capabilities to perform satisfactorily.

24. AWARD CRITERIA

24.1 	Subject to ITB Clause 28, the Purchaser will award the contract to the successful bidder whose bid has been determined to be substantially responsive and has been determined as the lowest evaluated bid, provided further that the bidder is determined to be qualified to perform the contract satisfactorily.

25. PURCHASER’S RIGHT TO VARY QUANTITIES AT TIME OF AWARD

  - The Purchaser reserves the right at the time of award of contract to increase or decrease the quantity of goods and services originally specified in the bid document without any change in unit price or other terms and conditions with in the bid validity period.

  - The quantity mentioned herein is present requirement and in case more or less quantity is required, the suppliers should be prepared to effect supply at short notice on the same terms and conditions.

26. PURCHASER’S RIGHT TO ACCEPT ANY BID AND TO REJECT ANY OR ALL BIDS

26.1 		The Purchaser reserves the right to accept or reject any bid, and to annul the bidding process and reject all bids at any time prior to award of Contract, without thereby incurring any liability to the affected bidder or bidders.

27. NOTIFICATION OF AWARD

27.1 	Prior to the expiration of the period of bid validity, the Purchaser will notify the successful bidder in writing by registered letter or by cable, that its bid has been accepted.

27.2	The notification of award will constitute the formation of the contract

28.      DELETED

29. DELAYS IN EXECUTION OF ORDER

29.1	The supplier shall supply, install and hand over the entire equipment on turnkey basis within 30 days from the date of placing the Purchase Order/LOI.

29.2 	A delay by the Supplier in the performance of its delivery obligations shall render the Supplier liable to the imposition of penalty, unless an extension of time is agreed upon pursuant to Purchaser’s Order, without the application of liquidated damages.

  - If the Supplier fails to deliver any or all of the equipment or perform the Services within the time period(s) specified in the Purchase Order, the purchaser shall, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as penalty, a sum equivalent to the percentage specified in the SCC clause 10.

SECTION III

GENERAL CONDITIONS OF CONTRACT

GENERAL CONDITIONS OF CONTRACT

1. DEFINITIONS

1.1	In this contract the following terms shall be interpreted as indicated:

(a)  “The Contract” means the agreement entered into between the Purchaser and the Supplier as recorded in the Contract Form signed by the parties, including all the attachments and appendices thereto and all documents incorporated by reference therein;

(b) “The Contract Price” means the price payable to the Supplier under the Contract for the full and proper performance of its contractual obligations;

(c) “The Goods” means all the products, equipment, machinery, and/or other materials which the Supplier is required to supply to the Purchaser under the Contract;

(d) “Services” means services ancillary to the supply of the Goods, such as transportation and insurance, and other incidental services, such as installation, commissioning, provision of technical assistance, training and other obligations of the Supplier covered under the contract;

(e) “GCC” means the General Conditions of Contract contained in this section.

(f) “SCC” means the Special Conditions of Contract.

(g) “The Purchaser” means the Organization purchasing the Goods, as named in SCC;

(h) “The Supplier” means the individual or firm supplying the Goods under this Contract;

(i)  “Day” means calendar day.

(j)  “Delivery period” means the period applicable upto completion of supply; installation and testing by the supplier at the required location mentioned in purchase order and accepted by the Purchaser.

(k) “Earnest Money Deposit”(EMD) means Bid Security /monetary or financial guarantee to    	be furnished by a tenderer along with Technical Bid Documents.

2. APPLICATION

2.1	These General Conditions shall apply to the extent that they are not superseded by provisions in other parts of the Contract.

3. STANDARDS

3.1	The equipment supplied under this Contract shall conform to the standards mentioned in the Technical Specifications, and, when no applicable standard is mentioned, to the authoritative standard appropriate to the Goods’ country of origin and such standards shall be the latest issued by the concerned institution.

4. USE OF CONTRACT DOCUMENTS AND INFORMATION

4.1 	The Supplier shall not, without the Purchaser’s prior written consent, disclose the Contract, or any provision thereof, or any specification, plan, drawing, pattern, sample or information furnished by or on behalf of the Purchaser in connection therewith, to any person other than a person employed by the Supplier in performance of the Contract. Disclosure to any such employed person shall be made in confidence and shall extend only so far as may be necessary for purposes of such performance.

4.2	The Supplier shall not, without the Purchaser’s prior written consent, make use of any document or information enumerated in GCC Clause 4.1 except for purposes of performing the Contract.

4.3	Any document, other than the Contract itself, enumerated in GCC clause 4.1 shall remain the property of the Purchaser and shall be returned (in all copies) to the Purchaser on completion of the supplier’s performance under the Contract if so required by the Purchaser.

5. PATENT RIGHTS

5.1	The Supplier shall indemnify the Purchaser against all third-party claims of infringement of patent, trademark or industrial design rights arising from use of the Goods or any part thereof in India.

6. INSPECTION AND TESTS

6.1	The Purchaser or its representative shall have the right to inspect and/or to test/ or to ask the bidder for live demonstration of the Goods to confirm their conformity to the Contract at no extra cost of the Purchaser. The Special conditions of Contract and/or the Technical Specifications shall specify/or inform the bidder during technical evaluation what inspections and tests and demonstration the Purchaser requires and where they are to be conducted. The Purchaser shall notify the Supplier in writing of the identity of any representatives retained for these purposes.

6.2	The inspections and test may be conducted on the premises of the Supplier or its subcontractor(s) before despatch, or at the point of delivery and/or at the Goods final destination. Where conducted on the premises of the Supplier or its subcontractor(s), all reasonable facilities and assistance including access to drawings and production data etc. shall be furnished to the inspectors at no charge to the Purchaser.

6.3	Should any inspected or tested Goods fail to conform to the specifications, the Purchaser may reject them and the Supplier shall either replace the rejected Goods or make all alternations necessary to meet specification requirements free of cost to the Purchaser.

6.4 	The Purchasers right to inspect, test and, where necessary, reject the Goods’ on arrival at site shall in no way be limited or waived by reason of the Goods having previously been inspected, tested and passed by the Purchaser or its representative prior to the Goods dispatched.

7. Deleted

8 DELIVERY AND DOCUMENTS

8.1	Delivery destination for present estimated requirement of the Goods is within designated Hospital in Kerala State [as detailed in Section XVIII Consignee details]. The equipment supplied and installed shall be in accordance with the terms specified in the purchase order by the Purchaser. The documents like warranty certificate, equipment manual, test certificate and also other documents are to be furnished by the Contractor as specified in the tender/purchase order.

9.  Deleted

10.  INCIDENTAL SERVICES

10.1 	The supplier may be required to provide any or all of the following services, including additional services, if any, specified in SCC:

(a) Performance or supervision of the on-site assembly and/or start-up of the supplied goods

(b) Furnish tools required for assembly and/or maintenance of the supplied Goods;

(c) Furnish detailed operations and maintenance manual for each product

(d) performance or supervision or maintenance and/or repair of the supplied Goods, for a period of time agreed by the parties, provided that this service shall not relieve the Supplier of any warranty obligations under this Contract;

(e) Provide Training to the Purchaser’s Personnel, at the Supplier’s plant and/or on-site, in assembly, start-up, operation, maintenance and/or repair of the supplied Goods.

11 SPARE PARTS

11.1 	As specified in the Special Conditions of Contract, the Supplier may be required to provide any or all of the following materials and notifications and information pertaining to spare parts manufactured or distributed by the Supplier:

(a)Such spare parts as the Purchaser may elect to purchase from the Supplier, providing that this election shall not relieve the Supplier of any warranty obligations under the Contract; and

(b) In the event of termination of production of the spare parts;

(i) Advance notification to the Purchaser of the pending termination, in sufficient time to permit the Purchaser to procure needed requirements; and

(ii) Following such termination, furnishing at no cost to the Purchaser, the blueprints, drawings and specifications of the spare parts, if and when requested.

12. WARRANTY

12.1 	The Supplier warrants that the Goods supplied under this Contract are new, unused, of the most recent or current models and incorporate all recent improvements in design and materials unless provided otherwise in the Contract. The supplier further warrants that the Goods supplied under this Contract shall have no defect arising from design, materials or workmanship (except when the design and/or material is required by the Purchaser’s specifications) or from any act or omission of the Supplier, that may develop under normal use of the supplied Goods in conditions obtaining in the state/country of final destination

12.2 	This warranty shall remain valid for Two year after the Goods or any portion thereof as the case may be, have been delivered to and accepted at the final destination indicated in the Contract.

12.3 	The Purchaser shall promptly notify the supplier in writing of any claims arising under this warranty.

12.4 	Upon receipt of such notice, the Supplier shall, within the period specified in SCC and with all reasonable speed, repair or replace the defective Goods or parts thereof, without cost to the Purchaser

12.5 	If the Supplier, having been notified, fails to remedy the defect(s) within the period specified in SCC within a reasonable period, the Purchaser may proceed to take such remedial action as may be necessary, at the Supplier’s risk and expense and without prejudice to any other rights which the Purchaser may have against the Supplier under the contract.

  - Deleted

13. PAYMENT

13.1	The method and conditions of payment to be made to the Supplier under the Contract shall be specified in the Special Conditions of Contract.

13.2	The Suppliers request(s) for payment shall be made to the Purchaser in writing, accompanied by an invoice in two copies describing, as appropriate, the Goods delivered and the services performed, and by documents in two copies, submitted pursuant to GCC Clause 8, and upon fulfillment of other obligations stipulated in the contract.

13.3	Payment shall be made promptly by the Purchaser but in no case later than sixty (60) days after submission of the invoice/claim by the Supplier.

13.4 	Payment shall be made in Indian Rupees

14. PRICES

14.1	Prices charged by the Supplier for Goods delivered and Services performed under the Contract shall not vary from the prices quoted by the Supplier in its bid, with the exception of any prices adjustments authorized in the special Conditions of Contract or in the Purchaser’s request for bid validity extensions, as the case may be.

15. CHANGE ORDERS

15.1	The Purchaser may, at any time by written order given to the Supplier, make changes within the general scope of the Contract in any one or more of the following:

- the place of delivery; or

- the services to be provided by the Supplier.

15.2 	If any such changes cause an increase or decrease in the cost of, or the time required for, the Supplier’s performance of any provisions under the Contract, an equitable adjustment shall be made in the Contract Price or delivery schedule, or both, and the Contract shall accordingly be amended. Any claims by the Supplier for adjustment under this clause must be asserted within thirty (30) days from the date of the Supplier’s receipt of the Purchaser’s change order.

16. CONTRACT AMENDMENTS

16.1 	Subject to GCC Clause 17, no variation in or modification of the terms of the Contract shall be made except by written amendment signed by the parties.

17. ASSIGNMENT

17.1 	The Supplier shall not assign, in whole or in part, its obligations to perform under the contract, except with the Purchaser’s prior written consent.

18. SUBCONTRACTS

18.1	The supplier shall notify the Purchaser in writing of all subcontracts awarded under the contract if not already specified in his bid. Such notification, in his original bid or later, shall not relieve the Supplier from any liability or obligation under the contract.

19. LIQUIDATED DAMAGES

19.1	Subject to SCC clause 10.1.

20. TERMINATION BY DEFAULT

20.1	The Purchaser may, without prejudice to any other remedy for breach of contract, by written notice of default sent to the supplier, terminate the Contract in whole or part;

(a)if the Supplier fails to execute any or all of the contracts within the time period(s) specified in the Contract, or within any extension thereof granted by the Purchaser, or

(b) if the Supplier fails to perform any other obligation(s) under the contract.

20.2	In the event the Purchaser terminates the Contract in whole or in part,  the Purchaser may procure, upon such terms and in such manner as it deems appropriate, Goods or Services similar to those unexecuted, and the Supplier shall be liable to the Purchaser for any excess costs for such similar Goods. However, the Supplier shall continue the performance of the Contract to the extent not terminated.

21.  FORCE MAJEURE

21.1	For purposes of this Clause “Force Majeure” means an event beyond the control of the Supplier and not involving the Supplier’s fault or negligence and not foreseeable. Such events may include, but are not limited to, acts of the Purchaser either in its sovereign or contractual capacity, wars or revolutions, fires, floods, epidemics, quarantine restrictions and freight embargoes.

21.2	If a Force Majeure situation arises, the Supplier shall promptly notify the Purchaser in writing of such conditions and the cause thereof. Unless otherwise directed by the Purchaser in writing, the Supplier shall continue to perform its obligations under the Contract as far as is reasonably practical, and shall seek all reasonable alternative means for performance not prevented by the force majeure event.

22. TERMINATION FOR INSOLVENCY

22.1 	The Purchaser may at any time terminate the Contract by giving written notice to the Supplier, if the Supplier becomes bankrupt or otherwise insolvent. In this event, termination will be without compensation to the Supplier, provided that such termination will not prejudice or affect any right of action or remedy, which has accrued or will accrue thereafter to the Purchaser.

23. RESOLUTION OF DISPUTES

23.1 	The Purchaser and the supplier shall make every effort to resolve amicably by direct informal negotiation any disagreement or dispute arising between them under or in connection with the Contract.

  - If, after thirty (30) days from the commencement of such informal negotiations, the Purchaser and the Supplier have been unable to resolve amicably a Contract dispute, either party may require that the dispute be referred for resolution to the formal mechanisms specified in the Special Conditions of Contract. These mechanisms may include, but or not limited to, conciliation mediated by a third Party, adjudication in an agreed national forum, and national arbitration.

  - The jurisdiction of any disputes, suits and proceeding arising out of the tender shall be only in the court of Thiruvananthapuram.

24. GOVERNING LANGUAGE

24.1 	Subject to ITB clause 6.1

25. APPLICABLE LAW

25.1 	The Contract shall be interpreted in accordance with the laws of the Union of India.

26. NOTICES

26.1 	Any notice given by one party to the other pursuant to this Contract shall be sent to other party in writing or by email to the other Party’s address specified in Special Conditions of Contract.

26.2 	A notice shall be effective when delivered or on the notice’s effective date, whichever is later.

27. TAXES AND DUTIES

27.1	Suppliers shall be entirely responsible for all taxes, duties, license fees, octroi etc., incurred until delivery of the contracted Goods to the Purchaser and commissioning, handing over.

SECTION IV

SPECIAL CONDITIONS OF CONTRACT

SPECIAL CONDITIONS OF CONTRACT

The following Special Conditions of Contract shall supplement the General Conditions of Contract. Whenever there is a conflict, the provisions herein shall prevail over those in the General Conditions of Contract. The Corresponding clause number of the General Conditions is indicated in parentheses.

1. DEFINITIONS (GCC Clause 1)

(a) The Purchaser is HLL Lifecare Limited, Akkulalm Factory, Thiruvananthapuram

2. INSPECTION AND TESTS (GCC Clause 6)

2.1	The following inspection procedures and tests are required by the Purchaser;

the supplier shall get each equipment inspected in manufacturer’s works and submit a test certificate and also guarantee/warranty certificate that the equipment conforms to laid down specifications.

2.2	The Purchaser or its representative shall inspect and/or test any or all the equipment to confirm their conformity to the Contract specifications, prior to dispatch from the manufacturer’s premises. Such inspection and clearance will not prejudice the right of the consignee to inspect and test the equipment on receipt at destination.

2.3	If the equipment fails to meet the laid down specifications the supplier shall take immediate steps to remedy the deficiency or replace the defective equipment to the satisfaction of the Purchaser.

3. INSURANCE (GCC Clause 9)

3.1	Deleted

4. INCIDENTAL SERVICE (GCC Clause 10)

4.1	The following services covered under GCC Clause 10 shall be furnished and the cost shall be included in the contract price:

(a) Unloading, safe storage and handling of consignment off site.

(b) On site assembly of the supplied goods, installation, testing and

commissioning of the equipment and requisite training.

(c) Furnishing of detailed operations and maintenance manual for each appropriate unit of supplied Goods.

(d)  Periodical Preventive maintenance at the site during warranty period in coordination with OEM and their service agents

(c) To settle the cost of consumables to be incurred by Purchaser at the time of preventive maintenance during warranty period and to submit the bills of such consumables to the purchaser for reimbursement.

5. SPARE PARTS (GCC Clause 11)

Add as Clause 11.2 to the GCC the following:

5.1	Supplier shall carry sufficient inventories to assure ex-stock supply of consumable spares for the Goods. Other main spare parts and components shall be supplied as promptly as possible but in any case within one week of placement of order.

6. WARRANTY (GCC Clause 12)

Substitute GCC Clause 12.2 by the following:-

6.1	This warranty shall remain valid for TWO year after goods or any portion thereof as the case may be, have been delivered to and accepted at the final destination indicated in the contract.

6.2     Any major repair pointed out by the Purchaser within the warranty period shall be rectified by the Supplier from the date of intimation within a period of 3 calendar days and commission the equipment to the satisfaction of the Purchaser. Failing which the Purchaser has the right to levy penalty on the Supplier per day or part thereof for each equipment until the equipments are repaired and commissioned to the satisfaction of the Purchaser.

6.3	The Supplier shall, in addition, comply with the performance and/ or consumption guarantees specified under the contract. If for reasons attributable to the Supplier, these guarantees are not attained in whole or in part, the Supplier shall at its discretion either:

- make such changes, modifications, and/or additions to the Goods or any part thereof as may be necessary in order to attain the contractual guarantees specified in the Contract at its own cost and expense and to carry out further performance tests in accordance with SCC 2:

  - Deleted.

7. PAYMENT (GCC Clause 13)

7.1 	Payment for Goods and Services shall be made in Indian Rupees as follows:

- No advance payment is payable.

- 70 % payment of the invoice value shall be made within 30 days on supply of equipments in good and acceptable condition and against documentary proof of supply at the IMCH, Medical College Hospital, Kozhikode, Kerala.

- 20% after Erection, Testing, Commissioning and Handing Over of the item and Warranty Certificate.

- The balance 10 % shall be paid against submission of final acceptance certificate issued by Hospital Authorities, after Erection, Testing, Commissioning and Handing Over of the complete system to the Hospital and against Performance Bank Guarantee for equal value, valid during warranty period. from the date of completion and handing over equipments on turnkey basis to the Purchaser

- The Performance Guarantee shall be released only on submission of proof of preventive maintenance done during the warranty period and  certificate issued by the Hospital Authorities stating the satisfactory performance of the equipment during the warranty period and other necessary documents.

8. PRICES (GCC Clause 14)

Substitute Clause 14.1 of the GCC with the following:

8.1	Prices payable to the Supplier as stated in the Contract shall not be subject to adjustment during performance of the Contract.

9. SUB CONTRACT (GCC Clause 18)

Add at the end of sub-clause 18.1 the following:

9.1	Sub-contract shall be only for bought-out items and sub-assemblies.

10. LIQUIDATED DAMAGES (GCC Clause 19)

For delays:

Substitute GCC Clause 19.1 by the following:

10.1	If the Supplier fails to deliver any or all of the Goods or perform of services within the time period(s) specified in the Contract, the Purchaser shall without prejudice to its other remedies under the Contract, deduct from the Contract Price, as liquidated damages, a sum equivalent to 0.5 percent of the delivered price of the delayed Goods or unperformed Services for each week of delay or part thereof until actual delivery or performance, up to a maximum deduction of 10 percent of the delayed Goods or Services contract price. Once the maximum is reached, the Purchaser may consider termination of the Contract.

11. Deleted.

12. COMPREHENSIVE MAINTENANCE CONTRACT (CMC):

12.1	During CMC period, any major repair pointed out by the Purchaser shall be rectified by the Supplier from the date of intimation within a period of 3 calendar days and commission the equipment to the satisfaction of the Purchaser. Failing which the Purchaser has the right to levy penalty on the Supplier per day or part thereof for each equipment until the equipments are repaired and commissioned to the satisfaction of the Purchaser.

12.2	The Supplier shall indicate clearly the free guarantee maintenance of the whole system supplied by the Supplier and the same should not be less than 7 year.

12.3	The Supplier shall also indicate separately post guarantee maintenance cost (CMC) of the entire system for 7 years subsequent to warranty maintenance period of Two years and shall clearly indicate year wise maintenance cost with probable cost of spares required for each year, in addition to comprehensive maintenance charges, as per Section XI.

SECTION V

TECHNICAL SPECIFICATIONS

1. Diesel Generator (DG) Set 40 KVA (Fully Automatic Generator with AMF Panel)

Technical Specifications: - 40KVA DG SET Should comprising of ENGINE, with standard fitted accessories coupled with Alternator, Diesel tank, starting battery with leads, and AMF control panel. - Engine should be Ashok Leyland/ Kirloskar/ Cummins/ Mahindra/ Equivalent brand and make - It should be silent D.G Set with Acoustic Enclosure. - Standard AMF control panel, inbuilt, Factory integrated along with the Generator, it should not be assembled outside. - It should CPCB, Approved systems. - MCB with Acoustic Enclosure as Per CPCB Norms - Water-cooled/ Air cooled, 4 Stroke/ 3 Stroke cylinders with electronic speed governor - Safety Key lock to prevent unauthorized use Unit. Power Rating; KVA; 40. Electric Power; Kwe; 32. Fuel Tank Capacity; Liters; 140. System Dc Voltage; V; 12. Aspiration; T/C. Battery Capacity; AH; 99. Engine HP Rated; HP; 52.5. No. of cylinders; 4/In-line. Governor used; Electronic. Supplied with all standard accessories and fixing and fitting with laying: - All are 1500 rpm, 50Hz, 415V.0.8 pf (lag), 3 Phase Generators - All are direct injection type, liquid cooled (with radiator) inline engines - All are fitted with engine tripping facility for low lube oil pressure and high water temperature - All are provided with emergency trip on canopy - All rotate anti clock wise when viewed from alternator end - Cables are 3½ / 4 core armoured aluminum - Alternators shall be Brushless type - Rating figure as per BS 5514 / ISO 3046 / ISO 8528 - Figures are as per standard reference conditions - Supplied DG Set with all standard accessories and fixing and fitting with laying and loading unloading at proposed site. - Minimum 50 Ltr of Diesel shall be filled at the time of commissioning of the DG at supplier’s cost. - User manual with trouble shooting guidance in English. - Commissioning, Installation and Training at end-user site.

TECHNICAL SPECIFICATIONS

Scope of Work

Scope of the work shall include Supply, Erection, Testing and Commissioning of 40 KVA, SILENT Diesel Generator Set with Central Pollution Control Board (CPCB-II) approved Acoustic Enclosure comprising of Diesel Engine with standard accessories coupled to Alternator mounted on Channel Iron Base Frame with Vibration Free Pads, complete with Fuel Tank having sufficient capacity for minimum 8 Hours of operation with Auto Main Failure (AMF) Control Panel and Batteries with the following features given below.

Make

Engine: Ashok Leyland / Kirloskar/ Cummins / Mahindra / Equivalent

Alternator: KIRLOSKAR ELECTRIC/ CROMPTON GRAVES/ STANFORD/ EQUIVALENT

Engine

The Engine shall be of Radiator Cooled, Three Stroke / Four Stroke, Three/ Four Cylinder confirming to relevant Standards.

Battery Charging Alternator shall be coupled with the Engine.

Lube Oil Pressure Gauge, Water Pressure Gauge, Water Temperature Gauge and Oil Temperature Gauge shall be provided in the Engine.

Additional 230V Battery Charger shall be provided external to the engine.

Engine shall be filled with first fill of (fresh) Lube Oil and Coolant.

Alternator

Alternator shall be of Brushless, Self-Excited type rated at 40 KVA.

Terminal Voltage of the Alternator shall be 3 Phase, 4151% Volts, 50 Hz, 0.8 Power Factor, Four Wire.

Insulation of the Alternator shall be Class-H.

Voltage of the Alternator shall be self-regulated through AVR.

Mounting

Engine and Alternator shall be mounted on a common MS fabricated base frame with AVM Pads.

AMF Control Panel

The Control Panel shall be fabricated with minimum 16 gauge CRCA sheet and painted with powder coated paint. Suitable size of Aluminum Buses shall use for incoming and outgoing termination.

The DG set shall work on Auto Main Failure (AMF) with all accessories such as Contactors having sufficient rating, AMF Relays etc. complete. AMF Relays etc. complete. AMF control shall be inbuilt, Factory integrated along with the Generator.

The operation, monitoring and control of the system shall be controlled with Micro-processor based Controller installed in the Control Panel.

CT (Current Transformer) provided for measuring current shall be of Class 0.5 and shall be of cast resin type. The CT’s provided shall be submitted with the test certificate from State Electrical Inspectorate.

Indication Lamps shall be provided in the control panel for ‘Load On’ and ‘Running’.

Suitable rating of MCCB with over load and short circuit protection shall be mounted in the Control Panel for the isolation of loads. MCB shall be provided for the isolation / protection of control circuit (No fuses shall be used).

The AMF Control panel shall have the following functional facilities

- Emergency Stop

- Fault Reset

- Auto Start

- Manual Start

- Meters displaying the parameters

- Voltage

- Current

- Frequency

- Speed (RPM)

- Oil Pressure

- Water Pressure

- KVA

- KW

- LED Indication for the faults

- Fail To Start

- Over Load

- Over Speed & Under Speed

- Low Oil Pressure

- Engine temperature High

- Battery Charging Alternator Fail

- Engine Hour Counter

Vendors

Vendors List of the switchgear and other accessories are given below.

MCB & MCCB		: SIEMENS

Contactor		: SIEMENS

CT			: KAPPA / INTRANS / Equivalent

Indication Lamps	: TECKNIK / SIEMENS / L&T

Meters			: COZERVE / RISHAB /AE

Acoustic Enclosure

Acoustic Enclosure shall be made of CRCA sheet having minimum 2 mm thickness and the walls of the enclosure insulated with fire retardant foam. Sound level at 1 Mtr shall be ≤75 dB. The DG set shall meet all the specifications/norms stipulated by Ministry of Environment and Forests, Central Pollution Control Board (CPCB) and State Electrical Inspectorate etc. Necessary Air Louvers shall be provided in the enclosure.

Battery

Battery shall be Sealed Maintenance Free type. Make and Technical Data of the Battery shall be mentioned in the offer.

Fuel Tank

Fuel Tank shall have sufficient capacity for minimum 8 Hours of operation of the DG Set. Fuel Gauge shall also be provided for the indication of the level of the fuel. Breather to be provided on the top of the tank.

Installation, Testing & Commissioning

Supply, Installation, Testing & Commissioning of the whole system shall be in the scope of the Supplier.

Minimum 50Ltr of Diesel shall be filled by the supplier for the commissioning the DG at free of cost.

Approval

Approval from statutory bodies shall be arranged by HLL

Warranty

1) The Engine, Alternator, Battery and other accessories shall be warrantee for a period of 24 Months from the date of commissioning. Necessary Certificates of Warranty shall be submitted along with the DG Set.

2) The Bidder has to ensure periodical Preventive Maintenance service during warranty period at the installed sites, in coordination with the OEM and its Service Agencies. The Performance Guarantee shall be released only on submission of proof of preventive maintenance done and satisfactory performance certificate from the Hospital Authorities during the warrantee period.

3) Breakdown Maintenance support, for entire warranty period, shall be provided within 8 Hours of intimation of breakdown.

4) Preventive Maintenance service& Breakdown maintenance service support from the part of DG supplier includes:

- Change of Engine oil, filter etc. The price of consumables like Engine Oil, Filter etc. actually to be paid by the Purchaser/Consignee at the destination, during preventive maintenance in Warranty period, shall be specifically mentioned by the Bidder in the Price Bid –(B). Such costs of consumables shall be reimbursed by HLL on submission of bills by the supplier to this effect with original bills of consumables after each preventive maintenance.

- Replacement of all requisite spares and accessories.

Annual Comprehensive Maintenance Contract (ACMC)

Bider shall extend Annual Comprehensive Maintenance Contract for the whole system for a period of SEVEN years after the completion of Performance Warranty period. Supplier has to provide service support within 8 Hours. Rate of Comprehensive Annual Maintenance Contract shall be quoted in the Format attached as ANNEXURE.

Special Conditions:

- Make and Model Number of Diesel Engine and Alternator shall be specifically mentioned in the Bid. Catalogue of the same shall also be attached with the offer.

- BHP of the Diesel Engine shall be mentioned in the Bid and the same shall be taken for the calculation of power conversion.

- Rate may be quoted in the specific Price Bid Format attached, price of the equipment in Price Schedule (I) and Cost of Consumables to be paid by the Purchaser/Hospital at the time of preventive maintenance during warranty period in Price Schedule (II) under SECTION - X

- Pre-Shipment Inspection and Testing may be conducted by the supplier in the presence of Engineer in charge of HLL, at its discretion.

- Test Certificates of Engine and Alternator shall be supplied along with the DG Set.

- All the Unloading and Leading works of the DG Set at the site shall be in the scope of the supplier.

- A competent Technical Person from the supplier shall be present at the time of Trial Run and for the successful Commissioning of the DG Set.

- Approval of Equallant make shall be strictly under the preview of HLL and HLL can accept / reject any makes coming under equallent without assigning any reason.

- Bider shall provide and co-ordinate Service/Technical support for Engine, Alternator and other accessories during the period of Performance Guarantee and AMC Period.

SECTION VI

QUALIFICATION CRITERIA

(Referred to in Clause 1 of ITB)

(a)	The bidder or the manufacturer whose product is offered must have manufactured and supplied DG set of 40 KVA or higher capacity in any one of the last 2 calendar years and should be satisfactorily functioning with no adverse report for at least one year on the date of bid opening.

(b) 	The bidder should furnish the information on past supplies and satisfactory performance in the Proforma given under Section - VIII.

(c) 	Bidders shall invariably furnish documentary evidence (Performance Certificate from Clients) in support of the satisfactory operation of the equipment as specified above.

(d)	The Bidder shall furnish data to support that he has the financial and production capacity to perform the contract and complete the supplies within the stipulated delivery period.

SECTION VII

PROFORMA FOR EQUIPMENT AND QUALITY CONTROL EMPLOYED BY THE MANUFACTURER

(Please attach detailed proforma incorporating the information given below)

BID NO……………………….

DATE OF OPENING……..

NAME OF THE BIDDER: ……………………………………..

(Note: All details should be related to the manufacturer for the items offered for supply).

1.	Name & Full address of the Manufacturer

(a) PAN No              (b). ECC Code                    ( c) IEC if applicable

(d) CST No               (e) TIN No                           (f)   Any other details

(g) Service Tax Regn no.

2.	(a) Telephone No.  				Office/Factory/Works

(b) Fax No.					Office/Factory/Works

(c) e-mail address

- Location of the manufacturing factory

- Details of arrangement for quality control of products such as laboratory, testing equipment etc

- Whether Goods are tested to any standard specification?  If so, copies of specifications & original test certificates should be submitted.

7. What is the lead-time for execution of order for mentioned quantity of the item?

SECTION VIII (a)

PROFORMA FOR PERFORMANCE STATEMENT

Proforma for Performance Statement (for a period of last 3 years)

### IFB NO: HLL/AFT/TDG/IVF/Equip/2014-15/IV

Name of the firm:

| Order placed by (Full Address of Purchaser) | Order No. and Date | Description Of ordered item | Quantity of ordered item | Value of order | Date of Completion of delivery | Remarks indicating reasons for late delivery, if any | Has the equipment been satisfactorily functioning? (Attach a certificate from the Purchaser/Consignee) |
| --- | --- | --- | --- | --- | --- | --- | --- |

Signature and Seal of the Bidder ...................................

........................................................................................

SECTION VIII (b)

## HLL LIFECARE LIMITED

Akkulam Factory

THIRUVANANTHAPURAM-695017

### IFB NO: HLL/AFT/TDG/IVF/Equip/2014-15/IV

INDEMINITY CLAUSE

If the supplier fails to execute the order within the time prescribed for the delivery of goods ordered or violates or infringes the existing rates as agreed to as mentioned in the supply order, the supplier shall and will indemnify the company against all loses or damages whatsoever to be incurred or sustained including the legal cost or expenses incurred by the company by reason of non-delivery of goods at agreed quantity and rate with in the time specified in the supply order.  The company will initiate legal action if the supplier fails to execute the supply order as per the schedule in the supply order for the actual loss suffered. No quantity tolerance will be permitted in this regard unless otherwise prior approval is taken by the company before despatching any excess quantity supplied which shall be returned back on freight to pay basis at the risk of the supplier.   Responsiveness of the Bid shall be at the discretion of HLL.

The supplier shall have no right to change the quantity stipulated in the supply order.

Bid pronounced Non Responsive by HLL shall be summarily rejected.

The decision of HLL will be final and no correspondence of this shall be entertained.

We have read and understood the above conditions and agree to abide   by the same.

PLACE:                                NAME AND SIGNATURE OF THE BIDDER

DATE:                                                          (WITH OFFICE SEAL)

SECTION VIII (c)

## HLL LIFECARE LIMITED

Akkulam Factory

THIRUVANANTHAPURAM-695017

### IFB NO: HLL/AFT/TDG/IVF/Equip/2014-15/IV

#### DECLARATION

I / WE, The Bidder undertake, we shall execute, with in the purview of the contract, all the works and activities includes; transportation, loading, unloading and other technical work for the installation of the equipment at the designated site as per the contract / purchase order, at IMCH, Medical College Hospital, Kozhikode, Kerala.

We confirm having read and understood all the specifications, instructions, forms, terms and conditions and other requirements of the above bid (both expressed and implied) in full and that we agree to abide by all without any deviation.

SEAL OF THE APPLICANT

SIGNATURE

NAME AND ADDRESS OF BIDDER

PART  B

SECTION IX

PRICE BID FORM

Date : ..............................

### IFB NO: HLL/AFT/TDG/IVF/Equip/2014-15/IV

To:

HLL Lifecare Limited,

Akkulam Factory,

Sreekariam P.O.

Thiruvananthapuram - 17

Dear Sir

Having examined the Bidding Documents including Addenda Nos......................, the receipt of which is hereby duly acknowledged, we, the undersigned, offer to supply and deliver...........................................

(Description of Goods and Services) in conformity with the said Bidding Documents for the sum of.............................. (Total Bid amount in Words and Figures) or such other sums as may be ascertained in accordance with the Schedule of Prices attached herewith and made part of this bid.

We agree to abide by price per unit mentioned in price schedule, for the bid validity period specified in the bid document and it shall remain binding upon us and may be accepted by you at any time before the expiration of that period.

Until a formal final contract is prepared and executed between us, this bid, together with your written acceptance of the bid and your notification of award, shall constitute a binding Contract between us. We understand that you are not bound to accept the lowest or any bid you may receive.

We confirm that we comply with the eligibility requirements as per ITB Clause 1 of the bidding documents.

Dated this ....... day of ............................ 20 ......

___________________________________

(signature)

(in the capacity of) ____________________

Duly authorized to sign Bid for and on behalf of

____________________________________

SECTION X

PRICE SCHEDULE (I)

Supply, Installation, Commissioning and handover DG Set 40 KVA  to Purchaser/IMCH, Medical College Hospital, Kozhikode

| Sl. No. | Item Description | Brand/Model | Manufacturer | Ex-factory price (Basic Unit Price exclusive of all levies & charges) | Excise Duty |  | Sales Tax |  | Insurance & Freight FOR Delivery destination |  | Service Tax (if any) |  | Unit Price inclusive of all levies & charges (ColumnNo. e+g+i+k+m) in Rs |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | % | Amt. | % | Amt. | % | Amt. | % | Amt. |  |
| a | B | c | d | e | f | g | h | I | j | k | l | m |  |
| 1 | Diesel Generator set 40 KVA (1 No) |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | Any other charges, bidder intends to mention (please specify)…………..………………………………………. |  |  |  |  |  |  |  |  |  |  |  |  |

Delivery schedule : strictly with in 30 days

NOTE:  1) The columns may be filled as is applicable in each case.

2) Bidders should bid for the entire quantity asked by the purchaser in the bid document.

Bidding for part quantity for any equipment will not be considered.

*** 3) Product catalogue  along WITH COMPLIANCE SHEET confirming to technical specification should be attached with offer.

*** 4) List of optional accessories/ spares with rate, to be attached to Price Bid as separate sheet

Seal and Signature of the bidder

SECTION X

PRICE SCHEDULE (II)

Price of the Consumables required in Preventive Maintenance of DG Set 40 KVA

during Warranty Period at IMCH, Medical College Hospital, Kozhikode

| Sl. No. | Description | Quantity required | Unit Price inclusive of all | Total Price all inclusive (Column No. c*d) in Rs |
| --- | --- | --- | --- | --- |
| a | B | c | d |  |
| 1 | Filter for DG set 40 KVA (1 No) |  |  |  |
| 2. | Oil for DG set 40 KVA (1 No) |  |  |  |
| 3 | Any other consumables, cost of which the Purchaser/Hospital is to be incurred (specify item) …………………………. |  |  |  |

NOTE:

1) 	List of Consumables required at the time of Preventive Maintenance during Warranty Period shall be clearly mentioned 			by the Bidder in column (b) Description above ESSENTIALLY.

Seal and Signature of the bidder

SECTION XI

CAMC Price Schedule -    Diesel Generator Set 40 KVA

| S.No. | Item Description | Brand/Model | Quantity | Year 1 Price | Year 2 Price | Year 3 Price | Year 4 Price | Year 5 Price | Year 6 Price | Year 7 Price | Grand Total Price (e+f+g+h+i+j+k) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| a | b | c | d | e | f | g | h | i | j | k | l |
| 1 | Diesel Generator set 40 KVA |  |  |  |  |  |  |  |  |  |  |
| 2 | Any other charges, bidder intends to mention (please specify)………….. ………………………………………. |  |  |  |  |  |  |  |  |  |  |

Scope of Contract : No of Visit (during the contract period)

a) Preventive maintenance visit: …………  b) Break down maintenance  visit:……..

“CMC” Comprehensive maintenance Contract includes; abors, spare and preventive & break down maintenance.

Note: Bidders should offer CAMC for the entire quantity asked by the purchaser in the bid document.

Part CAMC for part quantity for any equipment will not be considered.

Seal and Signature of the bidder

SECTION – XIII

BANK GUARANTEE FORM FOR EMD

Whereas ___________________ (hereinafter called the “Tenderer”) has submitted its quotation dated ___________________ for the supply of ____________________ (hereinafter called the “tender”) against the purchaser‟s tender enquiry No. __________________ Know all persons by these presents that we _________________________ of ______________________ (Hereinafter called the “Bank”) having our registered office at ________________________________________ are bound unto ____________________________ (hereinafter called the “Purchaser) in the sum of _________________________ for which payment will and truly to be made to the said Purchaser, the Bank binds itself, its successors and assigns by these presents.

Sealed with the Common Seal of the said Bank this ________day of _______ 20____. The conditions of this obligation are:

1) If the Tenderer withdraws or amends, impairs or derogates from the tender in any respect within the period of validity of this tender.

2) If the Tenderer having been notified of the acceptance of his tender by the Purchaser during the period of its validity:-

fails or refuses to furnish the performance security for the due performance of the contract or fails or refuses to accept/execute the contract or

if it comes to notice that the information/documents furnished in its tender is incorrect, false, misleading or forged

We undertake to pay the Purchaser up to the above amount upon receipt of its first written demand, without the Purchaser having to substantiate its demand, provided that in its demand the Purchaser will note that the amount claimed by it is due to it owing to the occurrence of one or both the two conditions, specifying the occurred condition(s). This guarantee will remain in force for a period of forty-five days after the period of tender validity and any demand in respect thereof should reach the Bank not later than the above date. …………………………….

(Signature with date of the authorised officer of the Bank)

………………………………………………………….

Name and designation of the officer

………………………………………………………….

………………………………………………………….

Seal, name & address of the Bank and address of the Branch

SECTION – XIV

MANUFACTURER‟S AUTHORISATION FORM

Joint General Manager (Materials)

HLL LIFECARE LIMITED

AKKULAM  FACTORY,

SREEKARIAM  P.O.

THIRUVANANTHAPURAM - 17

Dear Sir,

Ref: Your TE document No ____________ dated _____________

We, ____________________________ who are proven and reputable manufacturers of___________________________(name and description of the goods offered in the tender) having factories at_____________________, hereby authorise Messrs________________(name and address of the agent) to submit a tender, process the same further and enter into a contract with you against your requirement as contained in the above referred TE documents for the above goods manufactured by us. We also state that we are not participating directly in this tender for the following reason(s): ___________________________________________________________(please provide reason here).

We further confirm that no supplier or firm or individual other than Messrs. __________________________ (name and address of the above agent) is authorised to submit a tender, process the same further and enter into a contract with you against your requirement as contained in the above referred TE documents for the above goods manufactured by us. We also hereby extend our full warranty, CMC as applicable as per clause 15 of the General Conditions of Contract, read with modification, if any, in the Special Conditions of Contract for the goods and services offered for supply by the above firm against this TE document. We also hereby confirm that we would be responsible for the satisfactory execution of contract placed on the authorised agent We also confirm that the price quoted by our agent shall not exceed the price which we would have quoted directly”

Yours faithfully,

[Signature with date, name and designation]

for and on behalf of Messrs___________________________

[Name & address of the manufacturers]

Note: 1. This letter of authorisation should be on the letter head of the manufacturing firm and should be signed by a person competent and having the power of attorney to legally bind the manufacturer.

2.Orginal Letter may be sent. Photocopy not acceptable.

SECTION – XV

BANK GUARANTEE FORM FOR PERFORMANCE SECURITY/ CMC SECURITY

The Joint General Manager (Materials)

HLL LIFECARE LIMITED

AKKULAM  FACTORY,

SREEKARIAM  P.O.

THIRUVANANTHAPURAM - 17

WHEREAS _____________________________ (Name and address of the supplier) (Hereinafter called “the supplier”) has undertaken, in pursuance of contract no________________________ dated _____________ to supply (description of goods and services) (herein after called “the contract”). AND WHEREAS it has been stipulated by you in the said contract that the supplier shall furnish you with a bank guarantee by a scheduled commercial bank recognised by you for the sum specified therein as security for compliance with its obligations in accordance with the contract;

AND WHEREAS we have agreed to give the supplier such a bank guarantee;

NOW THEREFORE we hereby affirm that we are guarantors and responsible to you, on behalf of the supplier, up to a total of. __________________ (Amount of the guarantee in words and figures), and we undertake to pay you, upon your first written demand declaring the supplier to be in default under the contract and without cavil or argument, any sum or sums within the limits of (amount of guarantee) as aforesaid, without your needing to prove or to show grounds or reasons for your demand or the sum specified therein.

We hereby waive the necessity of your demanding the said debt from the supplier before presenting us with the demand.

We further agree that no change or addition to or other modification of the terms of the contract to be performed there under or of any of the contract documents which may be made between you and the supplier shall in any way release us from any liability under this guarantee and we hereby waive notice of any such change, addition or modification. This guarantee shall be valid up to 30 (thirty) months from the date of Notification of Award i.e. up to ----------- (indicate date) …………………………….

(Signature with date of the authorised officer of the Bank)

………………………………………………………….

Name and designation of the officer

………………………………………………

…………. …………………………

……………………………….

Seal, name & address of the Bank and address of the Branch

SECTION – XVI

CONTRACT FORM - A

CONTRACT FORM FOR SUPPLY, INSTALLATION, COMMISSIONING, HANDING OVER, TRIAL RUN, TRAINING OF OPERATORS & WARRANTY OF GOODS

……………………………..(Address of the Purchaser‟s/Consignee‟s office issuing the contract) Contract No___________ dated______________ This is in continuation to this office‟s Notification of Award No_______ dated ______ 1. Name & address of the Supplier: ______________________________ 2. Purchaser‟s TE document No________ dated____________ and subsequent Amendment No____________, dated_________ (if any), issued by the purchaser 3. Supplier‟s Tender No_________ dated__________ and subsequent communication(s) No____________ dated _________ (if any), exchanged between the supplier and the purchaser in connection with this tender. 4. In addition to this Contract Form, the following documents etc, which are included in the documents mentioned under paragraphs 2 and 3 above, shall also be deemed to form and be read and construed as integral part of this contract:

(i) General Conditions of Contract;

(ii) Special Conditions of Contract;

(iii) List of Requirements;

(iv) Technical Specifications;

(v) Quality Control Requirements;

(vi) Tender Form furnished by the supplier;

(vii) Price Schedule(s) furnished by the supplier in its tender;

(viii) Manufacturers‟ Authorisation Form (if applicable for this tender);

(ix) Purchaser‟s Notification of Award

Note: The words and expressions used in this contract shall have the same meanings as are respectively assigned to them in the conditions of contract referred to above. Further, the definitions and abbreviations incorporated under General Instructions to Tenderers‟ of the Purchaser‟s TE document shall also apply to this contract, Some terms, conditions, stipulations etc. out of the above-referred documents are reproduced below for ready reference:

(i) Brief particulars of the goods and services which shall be supplied/ provided by the supplier are as under:

a)…………………………….

b)………………………………

c)…………………………….. Any other additional services (if applicable) and cost thereof: ___________________ Total value (in figure) ____________ (In words) ___________________________

(ii) Delivery schedule

(iii) Details of Performance Security

(iv) Quality Control

(a) Mode(s), stage(s) and place(s) of conducting inspections and tests.

(b) Designation and address of purchaser‟s inspecting officer

(v) Destination and despatch instructions

(vi) Consignee, including port consignee, if any

6. Warranty clause

7. Payment terms

8. Paying authority

(Signature, name and address of the Purchaser’s/Consignee's authorised official)

For and on behalf of__________________

Received and accepted this contract

(Signature, name and address of the supplier‟s executive duly authorised to sign on behalf of the supplier)

For and on behalf of _________________________

(Name and address of the supplier)

(Seal of the supplier)

Date: _________________________ Place: _________________________

SECTION – XVII

CONSIGNEE RECEIPT CERTIFICATE

(To be given by consignee’s authorized representative)

The following store (s) has/have been received in good condition:

1) Contract No. & date :______________________________

2) Supplier’s Name :______________________________

3) Consignee’s Name & Address with telephone No. & Fax No. : ______________________________

4) Name of the item supplied :______________________________

5) Quantity Supplied :______________________________

6) Date of Receipt by the Consignee :______________________________

7) Name and designation of Authorized Representative of Consignee :______________________________

8) Signature of Authorized Representative of Consignee with date :______________________________

9) Seal of the Consignee :______________________________

SECTION – XVIII

Proforma of Final Acceptance Certificate by the Consignee

No_______________ Date_______________

To

M/s _______________________

_______________________

_______________________

Subject: Certificate of commissioning of equipment/plant.

This is to certify that the equipment(s)/plant(s) as detailed below has/have been received in good conditions along with all the standard and special accessories and a set of spares (subject to remarks in Para no.02) in accordance with the contract/technical specifications. The same has been installed and commissioned.

(a) Contract No______________________________________ dated_______________

(b) Description of the equipment(s)/plants: ____________________________________

(c) Equipment(s)/ plant(s) nos.:_____________________________________________

(d) Quantity: ____________________________________________________________

(e) Name of the vessel/Transporters:__________________________________________

(f) Name of the Consignee:_________________________________________________

(g) Date of commissioning and proving test:____________________________________

Details of accessories/spares not yet supplied and recoveries to be made on that account.:

| Sl. No. | Description of Item | Quantity | Amount to be recovered |
| --- | --- | --- | --- |

The proving test has been done to our entire satisfaction and operators have been trained to operate the equipment(s)/plant(s).

The supplier has fulfilled its contractual obligations satisfactorily ## or

The supplier has failed to fulfil its contractual obligations with regard to the following:

a) He has not adhered to the time schedule specified in the contract in dispatching the documents/ drawings pursuant to „Technical Specifications‟.

b) He has not supervised the commissioning of the equipment(s)/plant(s)in time, i.e. within the period specified in the contract from date of intimation by the Purchaser/Consignee in respect of the installation of the equipment(s)/plant(s).

c) The supplier as specified in the contract has not done training of personnel.

The extent of delay for each of the activities to be performed by the supplier in terms of the contract is The amount of recovery on account of non-supply of accessories and spares is given under Para no.02. The amount of recovery on account of failure of the supplier to meet his contractual obligations is_____________ (here indicate the amount).

(Signature) (Name)

(Designation with stamp)

## Explanatory notes for filling up the certificate:

i) He has adhered to the time schedule specified in the contract in dispatching the documents/drawings pursuant to „Technical Specification‟.

ii) He has supervised the commissioning of the equipment(s)/plant(s) in time, i.e. within the time specified in the contract from date of intimation by the Purchaser/Consignee in respect of the installation of the equipment(s)/plant(s).

iii) Training of personnel has been done by the supplier as specified in the contract.

iv) In the event of documents/drawings having not been supplied or installation and commissioning of the equipment(s)/plant(s) having been delayed on account of the supplier, the extent of delay should always be mentioned in clear terms

Section – XXI

Consignee List

| Delivery Site Address | IMCH Medical College Hospital, Kozhikode, Kerala |
| --- | --- |

SECTION XII

CHECK LIST

| Sl No. | Documents | Page No. | Remarks |
| --- | --- | --- | --- |
| 1 | Bid Security in the form of DD drawn in favor of HLL Lifecare Limited, Payable at Thiruvananthapuram |  |  |
| 2 | EMD in the form of DD drawn in favor of HLL Lifecare Limited, Payable at Thiruvananthapuram / Bank Guarantee |  |  |
| 3 | Market standing certificate to prove that the bidder manufactures the quoted items for the past 3 years |  |  |
| 4 | Duly attested copy of factory license/ Industrial license |  |  |
| 5 | Duly attested copy of sales tax registration certificate |  |  |
| 6 | Duly attested copy of document to prove the legal status, place of registration and principal place of business of the undertaking |  |  |
| 7 | Duly attested copies of quality certificates for the products and quality system certifications |  |  |
| 8 | Copy of Balance sheet for the past financial years, duly certified by a chartered accountant |  |  |
| 9 | Copy of Profit & Loss Account for 3 years certified by chartered accountant |  |  |
| 10 | Duly filled proforma showing details of Equipment and Quality Control of the manufacturer as per section VII |  |  |
| 11 | Proforma for Performance Statement (for a period of last 3 years) as per Section VIII |  |  |
| 12 | Self attested statement showing financial capability necessary to perform the Contract |  |  |
| 13 | Self attested statement showing technical and execution capability necessary to perform the Contract as per Section VI |  |  |
| 14 | Client's Certificate as per Section VI |  |  |
| 15 | Product brochure literature, write up etc. |  |  |
| 16 | Item-by-item commentary (compliance statement) on the Purchaser’s Technical Specifications demonstrating substantial responsiveness of the goods and services to those specifications or a statement of deviations and exceptions to the provisions of the Technical Specifications |  |  |
| 17 | The letter of authorization indicated by written power-of-attorney |  |  |
| 18 | Spare parts and after sales service facilities in India |  |  |
| 19 | Documentary evidence of constitution of firm such as Memorandum of Articles, Partnership Deed, etc., with details of Name, Address, Tel. No., Fax No., E-mail Address of firm and the Managing Director / Partner / Proprietor |  |  |
| 20 | Annual turnover statement for last 3 years certified by the Auditor |  |  |
| 21 | List of items quoted (without prices) |  |  |