## Civil abstract-3
CONSTRUCTION OF MICROBIOLOGY LAB WITH BSL II FACILITY AT CHIEF DISEASE INVESTIGATION OFFICE, PALODE.
PART 1 - CIVIL WORKS
Item No | Description of Item | Quantity | Unit | Rate (Rs. In Figures & Words) | Amount
SUB HEAD - I -EARTH WORK
1 | Clearing jungle including uprooting of rank vegetation, grass, brush wood, trees and saplings of girth upto 30 cm measured at a height of 1m above ground level and removal of rubbish upto a distance of 50 m outside the periphery of the area cleared. | 750 | SQM
2 | Felling trees of the girth (measured at a height of 1 m above ground level) including cutting of trunks and branches removing the roots and stacking of serviceable material and disposal of unserviceable material
a | Beyond 30 cm girth upto and including 60 cm girth | 15 | each
b | Beyond 60 cm girth upto and including 120 cm girth | 10 | each
3 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | 1130 | cum
4 | Extra for every additional lift of 1.5m or part in all kinds of soil
a | For lift up to 1.5 to 3 m | 20 | cum
5 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | 250 | CUM
6 | Diluting and injecting chemical emulsion for POST-CONSTRUCTIONAL anti-termite treatment (excluding the cost of chemical emulsion) :Along external wall where the apron is not provided using chemical emulsion @ 7.5 litres / sqm of the vertical surface of the substructure to a depth of 300 mm including excavation channel along the wall & rodding etc. complete:With Chlorpyriphos/ Lindane E.C. 20% with 1% concentration | 83 | m
SUB HEAD - II - PLAIN CEMENT CONCRETE
7 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size). | 52 | cum
SUB HEAD - III - RUBBLE WORK
8 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) at plinth level with : Cement mortar 1:6 (1 cement : 6 coarse sand) | 35 | cum
SUB HEAD - IV - REINFORCED CEMENT CONCRETE
9 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing & reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. All works upto plinth level | 73 | cum
10 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing but excluding reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. All works above plinth level upto floor V level | 133 | cum
11 | Add for using extra cement in the items of design mix over and abovethe specified cement content therein. | 145 | qntl
12 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. Thermo Mechanically Treated bars | 31000 | kg
13 | Centering and shuttering including strutting, propping etc. and removal of form for :
a | Foundations, footings, bases of columns, etc. for mass concrete | 205 | sqm
b | Suspended floors, roofs, landings, balconies and access platform | 535 | sqm
c | Lintels, beams, plinth beams, girders, bressumers and cantilevers | 510 | sqm
d | Columns, Pillars, Piers, Abutments, Posts and Struts | 240 | sqm
e | Stairs, (excluding landings) except spiral-staircases | 10 | sqm
f | Edges of slabs and breaks in floors and walls.Under 20 cm wide | 235 | m
SUB HEAD V : BRICK WORK
14 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in:Cement mortar 1:6 (1 cement : 6 coarse sand) | 9 | cum
15 | Brick work with F.P.S bricks of class designation 75 in superstructure above plinth level upto floor V level in cement mortar 1:6 (1 cement: 6 coarse sand) | 230 | Cum
16 | Half brick masonry with bricks of class designation 75 in superstructure above plinth level upto floor V level in cm 1:4 (1 cement: 4 coarse sand) | 31 | sqm
17 | Extra for providing and placing in position 2 Nos 6mm dia. M.S. bars at every third course of half brick masonry. | 31 | sqm
SUB HEAD :VI GRANITE WORK
18 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade Area of slab over 0.50 sqm | 230 | sqm
19 | Providing edge moulding to 18 mm thick granite stone counters, Vanities etc., including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge. Granite work | 115 | m
SUB HEAD VII: WOOD WORK
20 | Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length ( hold fast lugs or dash fastener shall be paid for separately).Second class teak wood | 1.5 | cum
21 | Providing and fixing panelled or panelled and glazed shutters for doors, windows and clerestory windows, including ISI marked M.S. pressed butt hinges bright finished of required size with necessary screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer-in-charge. Second class teak wood 30 mm thick shutters | 24 | sqm
22 | Providing and fixing panelling or panelling and glazing in panelled or panelled and glazed shutters for doors, windows and clerestory windows (Area of opening for panel inserts excluding portion inside grooves or rebates to be measured). Panelling for panelled or panelled and glazed shutters 25 mm to 40 mm thick :Second class teak wood | 49 | sqm
23 | Providing 40x5mm flat iron hold fast 40cm long including fixing to frame with 10mm diameter bolts,nuts and wooden plugs and embedding in cement concrete block 30x10x15cm 1:3:6 mix(1 cement : 3 coarse sand : 6 graded stone aggregate 20mm nominal size | 216 | each
24 | Providing and fixing 18mm thick marine plywood exsterior grade of approved make for cup board shelves including neccessary screws, nails,gum etc complete asper the direction of engineer-in - charge | 45 | sqm
25 | Providing and fixing Pre-laminated with (one side decorative and other side balancing lamination) flat pressed, 3 layer or graded particle board (medium density) Grade I, Type II, IS :12823 marked, with necessary fixing arrangements and screws, hinges etc. including drilling necessary holes for rawl plugs etc. and priming coat on unexposed surface complete :18 mm thick for cub board shutters | 31 | sqm
26 | Providing and fixing bright finished brass 100 mm mortice latch and lock with 6 levers and a pair of lever handles with necessary screws etc. complete (best make of approved quality). | 25 | each
27 | Providing and fixing bright finished brass butt hinges with necessary screws etc. complete : 125x70x4 mm (ordinary type) | 238 | each
SUB HEAD VIII: STEEL WORK
28 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete. Fixed to openings /wooden frames with rawl plugs screws etc | 1004 | Kg
29 | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of SS 304 grade 45X45mm square pipe frame with 30x6mm flat etc including necessary nuts and bolts and aluminium beeding to support the roofing, etc complete | 29.5 | m2
30 | Providing and fixing M.S. fan clamp type I of 16 mm dia M.S. bar bent to shape with hooked ends in R.C.C. slabs during laying including painting the exposed portion of loop , all as per standard design complete . | 21 | each
SUB HEAD IX : FLOORING
31 | Providing and fixing Ist quality ceramic glazed joint free wall tiles conforming to IS: 15622 Of thickness 5MM of approved make JOHNSON, NITCO, ORIENT, , KAJARIA or approved make, in all colours, shades except burgundy, bottle green, black of 600 x 300 mm as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. | 55 | sqm
32 | Providing and laying Ceramic joint free antiskid floor tiles of size 300x300 mm thicknes 7.5mm of 1st quality conforming to IS : 15622, of JOHNSON, NITCO, ORIENT, KAJARIA or approved make, in all colours, shades, except White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick bed of cement mortar 1:4 (1 Cement : 4 Coarse sand), including pointing the joints with white cement and matching pigments etc., complete. | 12 | sqm
33 | Providing and laying vitrified floor tiles in different sizes of 10mm thickness with water absorption less than 0.08% and conforming to IS : 15622, of jOHNSON, NITCO, ORIENT, KAJARIA or approved make approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand), including grouting the joints with white cement and matching pigments etc., complete. of size 600 x 600mm | 240 | sqm
34 | Cement concrete 1:2:4 with 20mm broken stone for flooring concrete in labs | 5 | m3
35 | Providing high performance seam less R-25CE of Endura or Equivalent epoxy resin floor system of hard wearing-durable, resistant to chemicls of approved colour 2mm thick including providing self levelling layer over hard concrete floorin one cc 1:2:4 with 20mm broken stone (cost of concrete will be paid seperately) | 60 | sqm
SUB HEAD X : ROOFING
36 | Providing and fixing false ceiling at all height including providing and fixing of frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) as per IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mm thick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, one flange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with 6mm dia bolts other flange of cleat fixed to the angle hangers of 25x10x0.50 mm of required length with nuts & bolts of required size and other end of angle hanger fixed with intermediate G.I. channels 45x15x0.9 mm running at the rate of 1200 mm centre to centre to which the ceiling section 0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm each having lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in a direction perpendicular to G.I. intermediate channel with connecting clips made out of 2.64 mm dia x 230 mm long G.I. wire at every junction, including fixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20 mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @ 230 mm interval, including fixing of gypsum board to ceiling
| section and perimeter channel with the help of dry wall screws of size 3.5 x 25 mm at 230 mm c/c, including jointing and finishing to a flush finish of tapered and square edges of the board with recommended jointing compound , jointing tapes , finishing with jointing compound in 3 layers covering upto 150 mm or both sides of joint and two coats of primer suitable for board, all as per manufacturer’s specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed, all complete as per drawings, specification and direction of the Engineer in Charge but excluding the cost of painting with :12.5 mm thick tapered edge gypsum moisture resistant board. | 85 | sqm
37 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes. 110 mm diameter | 35 | m
38 | Providing and fixing unplasticised -PVC pipe clips of approved design to unplasticised - PVC rain water pipes by means of 50x50x50 mm hard wood plugs, screwed with M.S. screws of required length including cutting brick work and fixing in cement mortar 1:4 (1 cement : 4 coarse sand) and making good the wall etc. complete - 110 mm | 25 | each
39 | Providing and fixing to the inlet mouth of rain water pipe cast iron grating 15cm diameter and weighing not less than 440 grams. | 6 | each
40 | Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion. bend 87.5 degree
a | 110 mm coupler | 10 | each
b | 110mm singel tee with door | 5 | each
c | 110 mm bend. | 25 | each
d | 110 mm shoe | 10 | each
41 | Providing and fixing semicircular 110mm PVC pipe for gutter with iron brackets 40 x 3 mm size, bolts , nuts and washers including making necessary connections with rain water pipes complete. | 10 | Meter
SUB HEAD XI : FINISHING
42 | 6 mm cement plaster of mix:1:3(1 cement:3 fine sand) | 570 | sqm
43 | 15mm cement plaster on rough side of single or half brick wall of mix 1:6 (1 cement : 6 coarse sand) | 40 | sqm
44 | 12 mm cement plaster of mix : 1:6 (1 cement: 6 coarse sand) | 1530 | sqm
45 | 18 mm cement plaster in two coats under layer 12 mm thick cementplaster 1:5 (1 cement : 5 coarse sand) finished with a top layer 6 mm thick cement plaster 1:6 (1 cement : 6 fine sand). | 580 | sqm
46 | Distempering with oil bound washable distemper of approved brand and manufacture to give an even shade : New work (two or more coats) over and including water thinnable priming coat with cement primer to under side of roof slab | 570 | sqm
47 | Finishing with Epoxy paint (two or more coats) at all locations prepared and applied as per manufacturer's specifications including appropriate priming coat, preparation of surface, etc. complete to the inside walls of lab | 205 | sqm
48 | Wall painting with plastic interior emulsion paint(premium quality) of approved brand and manufacture to give an even shade : Two or more coats on new work, over plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete including one coat of water thinnable cement primer of approved brand and manufacture on wall surface over putty | 1370 | sqm
49 | Wall painting with external emulsion paint of approved brand and manufacture to give an even shade: Two or more coats on new work, over one coat of water thinnable cement primer of approved brand and manufacture on wall surface . | 580 | sqm
50 | Polishing on wood work with ready mixed wax polish of approved brand and manufacture :New work | 150 | sqm
51 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :- Two or more coats to window grills | 63 | sqm
51 a | Painting wood work with Duluxe Multi Surface Paint of required shade. Two or more coat applied @ 0.90 ltr/10 sqm over an under coat of primer applied @0.75 ltr/ 10 sqm of approved brand or manufacture to shelves | 170 | sqm
SUB HEAD XII : MISCELLANEOUS
52 | Providing and fixing factory made uPVC door frame made of uPVC extruded sections having an overall dimension as below (tolerance ±1mm), with wall thickness 2.0 mm (± 0.2 mm), corners of the door frame to be Jointed with galvanized brackets and stainless steel screws, joints mitred and Plastic welded. The hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19 X 19 mm and 1mm (± 0.1 mm) wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturer’s specification and direction of Engineer- in-charge Extruded section profile size 48x40 mm | 20 | m
53 | 30 mm thick factory made Polyvinyl Chloride (PVC) door shutter made of styles and rails of a UPVC hollow section of size 60x30 mm and wall thickness 2 mm (± 0.2 mm), with inbuilt decorative moulding edging on one side. The styles and rails mitred and joint at the corners by means of M.S. galvanised/plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanised M.S. tube of size 25x20 mm and 1 mm (± 0.1 mm) wall thickness. The lock rail made up of 'H' section, a UPVC hollow section of size 100x30 mm and 2 mm (± 0.2 mm) wall thickness fixed to the shutter styles by means of plastic/ galvanised M.S. 'U' cleats. The shutter frame filled with a UPVC multi-chambered single panel of size not less than 620 mm, having over all thickness of 20 mm and 1 mm (± 0.1 mm) wall thickness . The panels filled vertically and tie bar at two places by inserting horizontally 6 mm galvanised M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer-in-charge. | 7 | sqm
SUB HEAD XIII : ALUMINIUM WORK
54 a | Providing and fixing aluminium work for doors, windows, ventilators and partitions withextruded built up standard tubular sections/ appropriate Z sections and other sections ofapproved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : a) For fixed portion . Powder coated aluminium (minimum thickness of powder coating 50 micron) of required colour as directed by the engineer in charge. | 730 | kg
b | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately) Powder coated aluminium (minimum thickness of powder coating 50 micron) of required colour as directed by the engineer in charge. | 483 | kg
c | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item):With float glass panes of 5.50 mm thickness | 85 | sqm
55 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture conforming to IS : 6315, having brand logo embossed on the body / plate with double spring mechanism and door weight upto 125 kg, for doors, including cost of cutting floors, embedding in floors as required and making good the same matching to the existing floor finishing and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per the direction of Engineer-in-charge. With stainless steel cover plate minimum 1.25 mm thickness | 2 | each
56 | Providing and fixing aluminium sliding door bolts ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete- | 1 | each
300x16mm
57 | Providing and fixing aluminium handles ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
a | 125 mm | 10 | each
b | 100mm | 10 | each
58 | Providing and fixing aluminium tower bolts ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
a | 250 X 10 mm | 20 | each
b | 150x10mm | 20 | each
59 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) Transparent or dyed to required colour and shade, with necessary screws etc. complete. Twin rubber stopper | 20 | each
60 | Supplying and fixing hand rails with 304 grade polished stainless steel pipe 2mm wall thickness for stair cases. 50mm diameter for hand rails and 100 mm dia for newel post and 25mm dia balusters 30cm c/c and 2nos horizontals welded together , including all neccessary fittings etc.. as per the drawing and direction of the Engineer – in – charge. Hand rails shall be fixed in the floor/steps with expansion hold fasters of required size including drilling etc.complete | 120 | kg
SUB HEAD : XIV WATER PROOFING
61 | 40 mm thick granite chips flooring to the top of roof slab, rubbed and polished to granolithic finish, under layer 28 mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 12.5 mm nominal size) and top layer 12 mm thick with black granite chips of sizes from 7 mm to 10 mm nominal size, laid in cement powder by weight in proportion of 2:3 (2 cement powder : 3 granite chips) by volume,including cement Slurry etc. complete by using Ordinary Portland cement | 430 | Sqm
SUB HEAD XV : SANITARY INSTALLATIONS& WATER SUPPLY
62 | Providing and fixing water closet squatting pan (Indian type W.C. pan ) with 100 mm sand cast Iron P or S trap, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever) conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required : White Vitreous china Orissa pattern W.C. pan of size 580x440 mm with integral type foot rests | 2 | each
63 | Providing and fixing white vitreous china pedestal type water closet (European type W.C.pan) with seat and lid, 10 litre low level P.V.C. flushing cistern with manually controlled device ( handle lever ), conforming to IS : 7231, Parryware / Hindware/ Seabrid / Orient ( Coral ) with all fittings and fixtures complete including cutting and making good the walls and flors wherever required :- | 2 | each
64 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require White Vitreous China Flat back wash basin size 550x 400 mm with single 15 mm C.P. brass pillar tap | 3 | each
65 | Providing and fixing P.V.C waste pipe for sink or wash basin, including P.V.C waste fittings complete :-
| Flexible pipe :-32 mm dia. | 3 | each
66 | Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors
| a)100mm inlet and 75mm outlet. | 5 | Each
67 | Providing and jointing PVC pipes of (pressure10 K g/cm2) for water supply including testing of joints, concealing the pipes , & trenching & refilling wherever required etc complete.
a | 20mm PVC pipe | 50 | Rm
b | 25mm PVC pipe | 50 | Rm
68 | Providing and fixing PTMT grating of approved quality and colour. 150 mm nominal size square 100 mm diameter of theinner hinged round grating | 2 | NOS
69 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. 15mm nominal bore | 3 | NOS
70 | Providing and fixing/laying unplasticised rigid P.V.C pipe conforming to IS Standards(pressure 6kg/cm2) in drainage lines including cutting and making good the walls,cutting and refilling of earth, jointing all etc complete
b | 110mm dia | 30 | Rm
c | 75mm dia | 60 | Rm
71 | Providing & fixing PVC Fittings and fixtures Conforming IS specifications including cutting and making good the walls etc complete
a | 110mm dia plain elbow | 5 | each
b | 75mm dia plain elbow | 10 | each
c | 110mm dia door elbow | 10 | each
d | 75mm dia door elbow | 10 | each
e | 110mm dia plain bend | 5 | each
f | 75mm dia plain bend | 10 | each
g | 110mm dia door tee | 5 | each
h | 75mm dia door tee | 10 | each
i | 110mm dia air cowl | 2 | each
j | 75mm dia air cowl | 2 | each
k | 110mm dia offset | 5 | each
l | 75mm dia offset | 10 | each
72 | Providing and fixing C.P. brass bib cock of approved qualityconforming to IS:8931 15mm nominal bore | 5 | each
73 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931. 15mm nominal bore | 7 | each
74 | Providing and fixing unplasticised P.V.C connection pipe with brass unions :- 45 cm length
a | 15MM nominal bore | 10 | each
75 | Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) –
| 32 mm dia nominal bore | 2 | each
76 | Providing and fixing ball valve (brass) of approved quality complete. High or low pressure with plastic floats 25 mm nominal bore | 2 | each
DRAINAGE
77 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m :Pipes, cables etc. exceeding 80 mm dia. but not exceeding 300 mm dia. | 60 | m
78 | Providing and fixing Porcelain Gully trap of 300 x 300 mm inside dimension for the waste line with cement concrete in1:4:8 (1cement:4coarse sand: 8 graded stone aggregate 40mm nominal size) for foundation and with necessary brick masonry in cement mortar 1:4(1cement:4coarse sand) and plastering with 12mm thick cement plaster in cement mortar 1:4 (1cement:4 fine sand) including neat cement flushing coat and providing RCC top slab with 1:2:4 mix etc complete | 2 | EACH
79 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 5 | each
80 | Extra for depth for manholes :- With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 3 | m
81 | Providing and fixing mirror of superior glass (of approved quality) and of required shape and size with plastic moulded frame of approved make and shade with 6 mm thick hard board backing : Rectangular shape 453x357 mm | 3 | each
82 | Providing and fixing C.P towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fittings arrangement of approved quality and colour.450 mm long towel rail with total length of 495 mm, 78 mm wide and effective height of 88 mm, weighing not less than 170 gms | 5 | each
83 | Providing and fixing C.P soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements, weighing not less than 106 gms. | 5 | each
84 | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of SS 304 grade 45X45mm square pipe frame with 30x6mm flat etc including necessary nuts and bolts and aluminium beeding to support the roofing, etc complete | 36 | m2
85 | Stone tile work for wall lining upto 10 m height with special adhesive over 12mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) including pointing in white cement with an admixture of pigment to match the stone shade 8mm thick (mirror polished and machine cut edge).Granite stone of any colour and shade.(colour should be selected by the engineer in charge) | 120 | m2
86 | Suspended walkable false ceiling with 75mm thick structural insulated sanwiched panels made with PUF insulation having density 40kg per cubic metre as core sandwiched between stainless steel sheet of thickness 0.6mm and grade SS 304-2B having 1200mm or suitable width with required length, consisting 'T'bar suspension type of frame work made with extruded aluminium perimeter channels and 3mm thick 1"x1"square tube extruded aluminium runners suspended with 6mm dia G>I> rods from existing RCC slab. Rate shall in dlude necessary cutouts for air supply and lluminaries complete with edge finishing. Silicon sealant shall be used at the joints. Ceiling system shall be suitable for loading upto 150kg/sq.m | 46 | m2
GRAND TOTAL - (PART I)