## steriodal
HLL LIFECARE LIMITED (Formerly Hindustan Latex Limited) (A Government of India Enterprise) KANAGALA – 591 225 HLL/BGM/PS/HVAC SYSTEM/13-14 14-01-2013
ANNEXURE – 3
SYSTEM DETAILS
Part A: OCP Sterioda section
Sr No | Name of the System | Area Covered | System Description | Air qty (CFM) | St.Pr. (mmWG) | Outdoor Unit (Tr) |  | Motor Rating (kW) | Filter Details
[6 empty] | Tr | Qty |  | Pre Filter (10 micro) | Micro (5 Micron) | Fresh Air (20 Micron) | Exhaust (0.3 Micron | HEPA (0.3 Micron) | Return 20 micron
1 | System 1A | Change Rooms - Gents (Supply) | Ventilation System | 1600 | 80 |  |  | 2.2 | 610x610x80 1 N0 | 610x610x305 1 N0 | NA | NA | 610×610×150 3 No[S]
2 | System 1B | Change Rooms - Gents (Exhaust) |  | 1600 | 50 |  |  | 2.2 | 610x610x80 1 N0 |  |  |  |  | 450x300, 3No
3 | System 2A | Change Rooms - Ladies (Supply) |  | 1600 | 80 |  |  | 2.2 | 610x610x80 1 N0 | 610x610x305 1 N0 |  |  | 610×610×150 3 No[S]
4 | System 2B | Change Rooms - Ladies (Exhaust) |  | 1600 | 50 |  |  | 2.2 | 610x610x80 1 N0 |  |  |  |  | 450x300, 3No
5 | System 11 A | Laundry - Supply |  | 4000 | 150 |  |  | 7.5 | 610x610x80 2 N0 | 610x610x305 2 N0 |  |  | 500x500x250, 5 No
6 | System 11 B | Laundry - Exhaust |  | 3000 |  |  |  |  | 610x610x80 2 N0 | 610x610x305 2 N0 |  |  |  | 750x450, 5No
7 | System 17 | Raw Material Sotre - Basement |  | 7000 | 125 |  |  | 5.5 | 610x610x50 4No | 610x610x300 4No |  |  | NA | NA
8 | System 20 | Airlock for Primary and Secondary Packing |  | 150 | 50 |  |  | 1.5 (1 Ph) | 300x300x50 1 No | 300x300x300 1 No |  |  | 300x300x300 1 No | NA
9 | System 3A | Granule Hold, Ipqc, Corridor, Sifter & Multimill Room For Dry Granules | Air Conditioned, Re-circulation type, 10% Fresh air, Minimum 20 to 40 Air changes per hour, Temperature maintained 25 ± 3º C, Relative Humidity NMT 65%, Class 100000 | 5000 | 150 | 8.5 | 1 | 7.5 | 610x762x80 2 No | 610x762x305 2 No | 300x300 1 No | 300x300 1 No | 610×610×75mm, 4 No 610x610x250, 6No | 350x300, 12No
10 | System 3B | Main Corridor |  | 5000 | 150 | 8.5 | 1 | 7.5 | 610x762x80 2 No | 610x762x305 2 No | 300x300 1 No | 300x300 1 No | 610×610×75mm,10 No | 350x300, 12No
11 | System 4 | Coating, Solution Preperation, Tablet Quarantine, Passed Tablet Quarantine |  | 5000 | 150 | 8.5 | 2 | 7.5 | 610x762x80 2 No | 610x762x305 2 No | 300x300 1 No | 300x300 1 No | 500x500x250, 8 No | 350x300, 4No 450x350, 5No
12 | System 5 | Compression 1 |  | 2200 | 150 | 5.5 | 1 | 3.7 | 762X610X80 1 No | 762X610X305 1 No | 200x200 1 No | 200x200 1 No | 610x610x250, 2 No | 850x450, 2No
13 | System 6 | Compression 2 |  | 2400 | 150 | 8.5 | 1 | 3.7 | 762X610X80 1 No | 762X610X305 1 No | 200x200 1 No | 200x200 1 No | 610x610x250, 3 No | 550x400, 4No
14 | System 7 | Punch Die Storage, Sifting, Drug Dispensing, Double Cone Blinder |  | 2500 | 150 | 5.5 | 1 | 3.7 | 762X610X80 1 No | 762X610X305 1 No | 200x200 1 No | 200x200 1 No | 610x610x200, 4 No | 250x300, 6No 550x400, 1No
15 | System 8 | Tray Dryer A |  | 1500 | 150 | 5.5 | 1 | 2.2 | 610x610x80 1 N0 | 610x610x305 1 N0 | 200x200 1 No | 200x200 1 No | 610x610x250, 2 No | 750x450, 2No
16 | System 9 | Tray Dryer B |  | 1500 | 150 | 5.5 | 1 | 2.2 | 610x610x80 1 N0 | 610x610x305 1 N0 | 200x200 1 No | 200x200 1 No | 610x610x250, 2 No | 750x450, 2No
17 | System 10 | RMG |  | 6000 | 150 | 8.5 | 2 | 7.5 | 610x610x80 2 N0 610x305x80 2NO | 610x610x305 2 N0 610x305x305 2 NO | 300x300 1 No | 300x300 1 No | 610x610x300, 6No | 850x450, 6No
18 | System 12 | Uncleaned Utilities Store, Wash Area, Cleaned Utilities Store |  | 2200 | 150 | 8.5 | 1 | 3.7 | 762X610X80 1 No | 762X610X305 1 No | 200x200 1 No | 200x200 1 No | 610x610x200, 3 No | 550x400, 3No
19 | System 13 | Blister Packaging 1 & 2, Blister Corridor, Tablet Inspection |  | 5000 | 150 | 5.5 | 2 | 7.5 | 610×610×50 2No | 610×610×300 2 No | 300x300x50 1 No | NA | 500x500x250, 8 No | 450x350, 7No 250x300, 4No
20 | System 14 | Sec.Packing,Blister Inspection |  | 3300 | 150 | 5.5 | 2 | 5.5 | 508x508x50, 4No | 610×610×300 4 No | 300x300x50 1 No |  | NA | 350x300, 8No
21 | System 15 | Finished Goods |  | 2000 | 125 | 8.5 | 1 | 2.2 | 610x610x50 1No | 610x610x300 1No | 150x150x50 1 No |  |  | 450x350, 4No
22 | System 16 | Raw Material Sotre - Ground Floor |  | 6600 | 125 | 5.5 | 3 | 7.5 | 610x610x50 4No | 610x610x300 4No | 300x300x50 1 No |  |  | 450x300, 13No
23 | System 18 | Sampling Booth |  | 1600 | 150 | 5.5 | 1 | 2.2 | 610x610x50 1No | 610x610x300 1No | 300x300x50 1 No |  | 610x610x250, 2No | 750x450, 2No
24 | System 19 | Dispensing Booth and Passage |  | 1600 | 150 | 8.5 | 1 | 2.2 | 610x610x50 1No | 610x610x300 1No | 300x300x50 1 No |  | 610x610x200, 4No | 450x300, 3No
25 | System 21 | Solvent Store |  | 2211 | 125 | 5.5 | 1 | 2 | 610x610x50 1No | 610x610x300 1No | 300x300x50 1 No |  | 300x300x300, 8No | 350x300, 6No

## Non st
HLL LIFECARE LIMITED (Formerly Hindustan Latex Limited) (A Government of India Enterprise) KANAGALA – 591 225 HLL/BGM/PS/HVAC SYSTEM/13-14 14-01-2013
ANNEXURE – 3
SYSTEM DETAILS
Part B: OCP Non-Sterioda section
Sr No | Name of the System | Area Covered | System Description | Air qty (CFM) | Static Pr (mmWG) | Outdoor Unit (Tr) |  | Motor Rating (kW) | Filter Details
[6 empty] | Tr | Qty |  | Pre Filter (10 micro) | Micro (5 Micron) | Fresh Air (20 Micron) | HEPA (0.3 Micron)
1 | System A | Coated Tablet Area | Air Conditioned, Re-circulation type, 10% Fresh air, Minimum 20 to 40 Air changes per hour, Temperature maintained 25 ± 3º C, Relative Humidity NMT 65%, Class 100000 | 563 | 125 | 1.73 | 1 | 2 | 406mm × 406mm × 50mm 1No [S]; | 610mm × 610mm ×150mm 1No[S]; | 300x300 1 No | 610mm × 610mm × 150mm 1No[S]
2 | System B | Coating Area |  | 1345 | 125 | 5.16 | 1 | 1.5 | 508mm × 508mm × 50mm 1No[S]; | 610mm × 610mm ×150mm 1No[S]; | 300x300 1 No | 610mm × 610mm × 150mm 1No[S]
3 | System C | Tab Quarantine. Tab Inspection |  | 1250 | 125 | 1.19 | 1 | 1.5 | 610mm × 610mm × 50mm 1No[S]; | 610mm × 610mm ×150mm 2Nos[S]; | 300x300 1 No | 610mm × 610mm × 300mm 2Nos[S]
4 | System D | Compression1 |  | 1545 | 125 | 2.46 | 1 | 1.5 | 635mm × 635mm × 50mm 1No[S]; | 610mm × 610mm ×150mm 2Nos[S]; | 300x300 1 No | 610mm × 610mm × 300mm 2Nos[S]
5 | System E | Compression2 |  | 1994 | 125 | 3.12 | 1 | 2.2 | 610mm × 610mm × 75mm 1No[S]; | 610mm × 610mm ×150mm 2 Nos[S]; | 300x300 1 No | 610mm × 610mm × 300mm 2Nos[S]
6 | System F | Blister Packing 1 |  | 2313 | 125 | 3.56 | 1 | 2.2 | 635mm × 635mm × 50mm 2Nos[S]; | 610mm × 610mm ×150mm 3Nos[S]; | 300x300 1 No | 610mm × 610mm × 300mm 3Nos[S]
7 | System G | Blister Packing 2 |  | 2313 | 125 | 3.56 | 1 | 2.2 | 635mm × 508mm × 50mm 2No[S]; | 610mm × 610mm ×150mm 3Nos[S]; | 300x300 1 No | 610mm × 610mm × 300mm 3Nos[S]
8 | System H | Washing Area, Shifting & Milling, and Granulation 1 & 2 | Ventilation System | 4000 | 100 | NA |  | 3.75 & 1.5 | 650mm × 550mm × 45mm 4No[S]; | 610mm × 610mm ×150mm 7Nos[S]; | NA | NA
9 | System I | Granulation holds, Corridor, Dispense hold, RM store, PM store, IPQC And Foils A/C store |  | 4000 | 100 |  |  | 3.75 & 0.75 | 610mm × 510mm × 50mm 2No[S]; | 610mm × 610mm ×150mm 4Nos[S]
10 | System J | Gents change room, Ladies change room, Secondary change room |  | 1500 | 100 |  |  | 2 & 0.75 | 630mm × 510mm × 50mm 1No[S]; | 610mm × 610mm ×290mm 1Nos[S]
11 | System K | Finished goods |  | 1500 | 100 |  |  | 0.75 & 0.14 | 450mm × 450mm × 50mm 1No[S]; | 450mm × 450mm ×95mm 1Nos[S]
12 | System L | Secondary packing |  | 1500 | 100 |  |  | 1.5 & 0.55 | 630mm × 510mm × 50mm 1No[S]; | 610mm × 610mm ×150mm 1Nos[S]

## BDU
HLL LIFECARE LIMITED (Formerly Hindustan Latex Limited) (A Government of India Enterprise) KANAGALA – 591 225 HLL/BGM/PS/HVAC SYSTEM/13-14 14-01-2013
ANNEXURE – 3
SYSTEM DETAILS
Part C: Bulk Drug Unit
Sr NO | Name of the System | DESCRIPTION | TR | MOTOR (KW) | Filter size
1 | System A | Sampling & Packing, Secondary Passage, Micro pulverising & Shifting, Try drier, IPQC, Wash and Clean area | 22 | 7.5 | 610mm × 610mm ×150mm 4Nos; 610mm × 610mm × 300mm 2 Nos; 300mm × 300mm × 300mm 7 Nos, & 400mm × 400mm 13 Nos; 600mm × 600mm 3 Nos;
Part D: Condom Secondary Section
Sr NO | Description | Area Covered | Air qnty (CFM) | MOTOR (KW) | Filter size
1 | Air Handling Unit | Packing, and Corridor | 20000 | 20 | 10 micron, 445mm × 445mm × 45mm 9Nos; 5 micron, 545mm × 545mm ×300mm 18Nos;
2 | Ambiator | Ambiator | 23000 | 15 | 610X610X150 20 Micrn filters 12 Nos
Part E: Details of Booth
Sr NO | DESCRIPTION | Area | Qty | Filter Details
1 | Sampling Booth | Raw Material Store, Non Steroidal | 2 | To be collected from site
2 | Dispensing Booth | Raw Material Store, Non Steroidal, Solvent Store, Compounding Section | 4
3 | Laminar Airflow | Laboratory | 1

## SECONDARY
ANNEXURE – 3
SYSTEM DETAILS
Part D: Condom Secondary Section
Sr NO | Description | Area Covered | Air qnty (CFM) | MOTOR (KW) | Filter size
1 | Air Handling Unit | Packing, and Corridor | 20000 | 20 | 10 micron, 445mm × 445mm × 45mm 9Nos; 5 micron, 545mm × 545mm ×300mm 18Nos;
2 | Ambiator | Ambiator | 23000 | 15 | 610X610X150 20 Micrn filters 12 Nos

## DISPENSING BOOTH
ANNEXURE – 3
SYSTEM DETAILS
Part E: Details of Booth
Sr NO | DESCRIPTION | Area | Qty | Filter Details
1 | Sampling Booth | Raw Material Store, Non Steroidal | 2 | To be collected from site
2 | Dispensing Booth | Raw Material Store, Non Steroidal, Solvent Store, Compounding Section | 4
3 | Laminar Airflow | Laboratory | 1